Distribution Network Reconfiguration for Loss Reduction

Figure 4.3: Voltage profile

using PSO Method

Yahiaoui Merzoug, Bouanane Abdelkrim,Boumediene Larbi

L.G.E Laboratory, Departement of Electrical Engineering, Dr. Moulay Taher University of SAIDA, Algeria

| Article Info |  | ABSTRACT (10 PT) |
| --- | --- | --- |
| Article history: ReceivedSep 9, 2019 Revised May 20, 2020 Accepted Jun 11, 2020 |  | In recent years, the reconfiguration of the distribution network has been proclaimed as a method for realizing power savings, with virtually zero cost. The current trend is to design distribution networks with a mesh network structure, but to operate them radially. This is achieved by the establishment of an appropriate number of switchable branches which allow the realization of a radial configuration capable of supplying all of the normal defects in the box of permanent defect. In this paper, the particle swarm optimization technique is used for optimal reconfiguration of the main distribution network. The objective of the proposed method is to reduce the total active power loss and voltage deviation experienced in the network. To test the efficiency of the proposed method and its practical distribution system, standard 33-bus test distribution network is used. The proposed algorithm is implemented in MATLAB and MATPOWER environments. The results obtained the effectiveness of the technical proposal. |
| Keywords: Particle Swarm Optimization Distribution Network reconfiguration Loss Reduction Voltage Profile |  |  |
|  |  | Copyright © 2020Institute of Advanced Engineering and Science. All rights reserved. |
| Yahiaoui Merzoug : L.G.E Laboratory, Departement of Electrical Engineering, Dr. Moulay Taher University of Saida, Algeria BP 138 En-Nasr, (20000 Saida), Algeria. Email: myahiaoui2001@yahoo.fr |  |  |

- INTRODUCTION

Electric power has become a consumer good worldwide for both everyday life and the economy of the country, and the smallest electrical problems have a great influence on the continuity of economic activities. Therefore, the possession of reliable and cost-effective electricity networks that function properly and ensure continuity of service and good quality energy has become essential to make a positive contribution to the development of our modern societies.

The distribution network must evolve into a flexible and intelligent network that best integrates local and / or renewable energies. The opening of the electricity market and growing environmental concerns related to global climate change are driving significant changes, particularly in the distribution networks, with the massive influx of decentralized products. This development can be envisaged by developing intelligent systems capable of minimizing the impacts generated by the insertion of decentralized productions and / or the search for new architectures. These two solutions should make it possible to increase the rate of decentralized production in the distribution network in the best economic and security conditions.

The major problem for network managers is to propose better planning for a better management of the transit of power. From the production centers to the consumer, transmission lines inflict large losses of energy, whether active or reactive, much more in the distribution networks where about 14% of the power transiting these lines is lost. All of these losses affect the quality of the voltage delivered to customers. For this purpose, the study of the power flow (Load flow) makes it possible to have the solution of the magnitudes of an electrical network in normal operation balanced in steady state. Load flow analysis in an electrical grid consisting of a number of generators, transmission lines and loads is very important for the design, planning and operation of an electrical network. The scheduler of this network can easily evaluate the impact of different transmission and generation configurations for any desired load level [28]. This makes it possible to know the conditions of production and load and the levels of the voltages of the network. and several remediation techniques are put into use to circumvent this problem. Among these solutions, we mention the decentralized productions that are increasingly present on the market. The conventional techniques used in decentralized production offer the network a better quality of energy, on the other hand their need for raw material as well as their impacts on the environment make of them undesirable means of production, on top of that their time and cost of realization are excessive [5]. For this decentralized production based on renewable energy is a promising alternative, the cost of implementation and maintenance is much lower than those mentioned before, their completion time is far shorter. On top of that, renewable energies are non-polluting. However, these are not magical solutions, because their impacts on the network and on the quality of energy impose the insertion of filtering, regulation and compensation means .

The incorporation of components such as FACTS devices and capacitors into the distribution system to reduce power losses comes with a high cost of implementation. It is necessary to reduce unnecessary expenses if there are better and cheaper alternatives to the costly options. Therefore, network reconfiguration which does not require any other additional components apart from switch manipulation of the already existing network system has been considered.

The objective of this technique is minimizing power loss and improves voltage.

- Mathematical model

0

1

i-1

i

i+1

n

P0 ,Q0

P1 , Q1

Pi -1, Qi-1

Pi , Qi

Pi+1 , Qi+1

PL1 ,QL1

PL1-1 ,QLi-1

PLi ,QLi

PL1+1 ,QLi+1

PLn ,QLn

Figure1. Single line diagram of radial feeder

The aim of this paper is to find the optimal location of the wind turbine in the network that will offer minimum power loss. Single line diagram of a simple feeder-line configuration is shown in figure.1.  a set of recursive equations for computation of power flow is given by [6]:

Pi+1=Pi-PLi+1-Ri,i+1.Pi2+Qi2Vi2                                                                (1)

Qi+1=Qi-QLi+1-Xi,i+1.Pi2+Qi2Vi2                                                                (2)

Vi+12=Vi2-2Ri,i+1.Pi+Xi,i+1.Qi. Pi2+Qi2Vi2                                                (3)

Where  , Pi and Qi are the real and reactive power flowing out of bus i; PLi+1 and QLi+1 are the real and reactive load powers at bus i+1.line section between buses i and i+1has resistance Ri,i+1and reactance Xi,i+1.voltage magnitude of bus i is Vi.for convergence of power flow ,the power balance equations (1)and (2) must be satisfied in addition, magnitudes of sending and receiving end bus voltages must satisfy equation(3).

The well known generalized formulas for real and reactive power loss in the line section between buses i and i+1 are calculated by using the following equations:

PLossi,i+1=Ri,i+1.Pi2+Qi2Vi2                                                                (4)

QLossi,i+1=Xi,i+1.Pi2+Qi2Vi2                                                                (5)

The total active and reactive power loss of the distribution system can be easily found by summing all of the branch power loss and it is expressed as:

Ptloss=i=1nbrPLossi,i+1                                                         (6)

Qtloss=i=1nbrQLossi,i+1                                                           (7)

Where, Ptloss is the total real power loss and Qtloss  is the loss incurred due to reactive power throughout the network. In this study we consider wind supplying real power with unity power factor.

3. Particle Swarm Optimization

3.1. Introduction

Particle swarm optimization (PSO) is a population-based optimization method first proposed by Kennedy and Eberhart in 1995, inspired by social behavior of bird flocking or fish schooling (Kennedy et al, 1995) [6]. The PSO as an optimization tool provides a population-based search procedure in which individuals called particles change their position (state) with time. In a PSO system, particles fly around in a multidimensional search space. During flight, each particle adjusts its position according to its own experience (This value is called Pbest), and according to the experience of a neighboring particle (This value is called Gbest), made use of the best position encountered by itself and its neighbor.[5]

In general, a PSO algorithm consists of three main steps, namely, 1) generate initial particle’s positions and velocities, 2) evaluate fitness value of each particle, and 3) update velocity and position of all particles. The first step is to allow all particles arbitrarily distributed across the search space. The second step is to evaluate fitness value of particles in order to determine the best position of each particle and to reveal the particle that has the best global fitness value in the current swarm. The third step updates the velocity of particles which are then used as the information for changing position of all particles.

In PSO, two different definitions are used: the individual best and the global best. As a particle moves through the search space, it compares its fitness value at the current position to the best fitness value it has ever attained previously. In PSO, to adjust the position, velocity of each particle is calculated using current position xi, best position of particle so far Pbest and global best position of particle in population Gbest. Velocity of each particle in the next generation can be calculated as:

(8)

Where  and  are random numbers between 0 and 1 while and  are positive constants, respectively. Inertia weight w is formulated as follows:

(9)

Where  and  are maximum and minimum of inertia weight, and are maximum iteration number and current iteration, respectively. Current position or searching point can be modified by the following equation.

The objective of the proposed technique is to minimize power loss and voltage deviation as formulated in objective function (OF) below.

𝑚𝑖𝑛 𝐹                                                                                           (10)

Where

𝐹=𝑓1+𝑓2                                                                              (11)

The first part of the OF is the index of power loss obtained by normalizing the power loss with its initial value as shown in (4)

f1=PlossreconfPlossinitial                                                                            (12)

WherePlossreconf, is the power loss after reconfiguration and Plossinitial is the power loss before reconfiguration calculated as;

Plossinitial=i=1nlRiPi2+Qi2Vi2for i=1,2…nl                                                    (13)

The second segment of the OF, f2 is the index of the total voltage deviation. It is similarly obtained by normalizing its reconfigured valueVdevreconf.  With its initial value, Vdevinitial.

f2=∆Vtotalreconf∆Vtotalinitial                                                                                    (14)

The total inherent voltage deviation is computed as;

ΔVtotalinitial=j=1NB1-Vj  for j=1,2,…NB                                                (15)

The DNR problem solved by considering the following constraints:-

4. Constraints

The constraints are listed as follows:

- Distribution line absolute power limits:

PijLine≤PijmaxLine                                                                    (16)

PijLine and PijmaxLine Are the absolute power and its corresponding maximum allowable value flowing over the distribution line between the nodes i and j, respectively.

- Bus voltage limit:

Bus voltage amplitudes are limited as

Vmin≤Vi≤Vmax                                                              (17)

Where Vmin  and Vmax  are the minimum and maximum values of bus voltage amplitudes, respectively.

CASE STUDIES

The system used for this method is tested on standard IEEE 33 bus test system as shown in Fig. 3. The system load is assumed to be constant with Sbase= 100MVA and  Vbase =12.66kV. The load and line data is referred in [10]. The total load of the system is 3715kW and 2300kVar. . All calculation is in per unit.

33

29

30

31

32

22

28

25

21

27

24

20

26

23

19

12	13	14	15	16	17	18

10	11

9

8

7

6

5

4

3

2

1

Figure.2. Single line diagram of 33 Bus electric distribution

The simulations were carried out by using MATLAB. The result with minimum power loss is selected as shown in Table I. The result consists of 5 opened switches, total power losses, voltage profile.Table 1

- Table 1. The Performance of ...

|  | Before Reconfiguration | After Reconfiguration |
| --- | --- | --- |
| Tie switches Power loss Minimum voltage Power loss reduction | 33 34 35 36 37 208.4592 kW 0.91075 pu - | 7 9 14 32 37 138.9275 kW 0.94234 pu 33.355 % |

The result show that the power losses for case 1 are 208.4592 kW and reduce to 33.355% for case 2. Fig. 3 shows the network reconfiguration switchers.

18

17

2

3

4

5

6

7

85

9

10

11

12

13

14

15

16

267

19

20

21

22

23

24

25

S1

S2

S3

S4

S5

S6

S7

S8

S9

S10

S11

S12

S13

S14

S15

S16

S17

S26

S27

S28

S29

S30

S31

S32

S24

S23

S19

S21

S33

S20

S35

S36

S37

275

28

29

30

31

32

33

Fig.3. Optimized Configuration of 33 bus test system

Fig. 4.3 shows the comparison of the voltage profile before and after network reconfiguration for case 1 and case 2, respectively. The network before reconfiguration is represented by case 1. The minimum voltage in case 1 was 0.91075p.u at node 18. With the PSO algorithm for optimum switching, the configuration in case 1 was converted into case 2. The result of voltage improvement became 0.94234p.u at node 32 as shown in case 2 of fig. 4.3.

Figure4. Voltage profile

The comparison for the real power losses in the branches is shown in fig.5 for the initial network before and after reconfiguration (case 1 and case 2), respectively, . The power losses in almost every branch in case 2 reduced, except at 18, 19, 20, 21, 33, 34 and 35, where there was a small increase in losses due to load shifting of the feeders altered by the switching as depicted in fig. 5.

Figure5. Real power losses in 33-bus system

- CONCLUSION (10 PT)

In this paper, the binary swarm optimization algorithm is applied to solve distribution network reconfiguration. The objective of the proposed technique is to minimize the active power loss and voltage deviation. It is carried out subject to some technical constraints in addition to maintaining the radial nature of the network.

It is envisioned as future work to incorporate distributed generation to support the loaded feeders. Same technique will be used to determine their optimal siting and sizing.

REFERENCES

- Wardiah Mohd Dahalan, Hazlie Mokhlis, “Network Reconfiguration for Loss Reduction with Distributed Generation Using PSO,” IEEE International Conference on Power and Energy (PEcon), 2-5 December 2012, Kota Kinabalu, Sabah, Malaysia.

- M.Padma Lalitha, V.C. Veera Reddy, V.Usha, “Optimal DG Placement for Minimum Real Power Losses in Radial Distribution System Using PSO,” Journal of Theoretical and Applied Information Technology ©2005-2010 JATIT.

- R.K. Singh and S.K. Goswami, “Optimum Allocation of Distributed Generation based on Nodal Pricing for Profit, Loss Reduction, and Voltage Improvement including Voltage Rise Issue,” Electrical Power and Energy System 32 (2012) 637-644.

- [Mohammad ShahabArkan and HamedSalehi, “Application of Particle Swarm Optimization for Optimal Distributed Generation Allocation to Voltage Profile Improvement and Line Losses Reduction in Distribution Network,” Research Journal of Applied Sciences, Engineering and Technology, 5(20):4791-4795, 2013.

- R. Eberhart, and J. Kennedy, "Particle Swarm Optimization," Proc. of IEEE International Conf. on Neural Networks, Vol. 4, pp. 1942 1948, 1995

- M. A. Kashem, M. Negnevitsky and G. Ledwich, "Maximising Voltage Support in Distribution Systems by    Distributed Generation," in TENCON 2005 - 2005 IEEE Region 10 Conference, Melbourne, Qld., Nov. 2005.

- M.H. Moradi and M. Abedini, “A Combination of Genetic Algorithm and Particle Swarm Optimization for Optimal DG location and Sizing in Distribution System,” Electrical Power and Energy System 34 (2012) 66-74.

- Yan Zhe-Ping, Deng Chao, Zhou Jia-Jia, Chi Dong-Nan, “A Novel Two-subpopulation Particle Swarm Optimization,” Proceedings of the 10th World Congress on Intelligent Control and Automation, July6-8,2012, Beijing, China.

- H. Li, W. Mao, A. Zhang, C. Li, "An improved distribution network reconfiguration method based on minimum spanning tree algorithm and heuristic rules," Electrical Power and Energy Systems, vol. 82, pp. 466-473, 2016.

- Y.C.Huang, “Enhanced genetic algorithm-based fuzzy multi objective  approach to distribution network reconfiguration”, Proc. Inst .Elect. Eng. 149 (5) (2002) 615–620.

- L. W. de Oliveira, F. S. Seta and E. J. de Oliveira, "Optimal reconfiguration of distribution systems with representation of uncertainties through interval analysis," Electrical Power and Energy Systems, vol. 83, p. 382–391, 2016

- O. Badran, S. Mekhilef, H. Mokhlis, and W. Dahalan, “Optimal switching sequence path for distribution network reconfiguration considering different types of distributed generation,” IEEJ Trans. Electr. Electron. Eng., vol. 12, no. 6, pp. 874–882, 2017.

- S. Jena and S. Chauhan, “Solving Distribution Feeder Reconfiguration and concurrent DG Installation problems for Power loss Minimization by MultiSwarm Cooperative PSO algorithm,” Proc. IEEE Power Eng. Soc. Transm. Distrib. Conf., vol. 2016–July, no. January, 2016.

- ]. Chiou, Ji-Pyng, Chung-Fu Chang, and Ching-Tzong Su. "Variable scaling hybrid differential evolution for   solving network reconfiguration of distribution systems." IEEE Transactions on Power Systems 20.2 (2005):

668-674.

- Yan Zhe-Ping, Deng Chao, Zhou Jia-Jia, Chi Dong-Nan, “A Novel Two-subpopulation Particle Swarm Optimization,” Proceedings of the 10th World Congress on Intelligent Control and Automation, July6-8,2012, Beijing, China.

BIOGRAPHIES OF AUTHORS (10 PT)

|  | Yahiaoui Merzoug is born in Saida (Algeria) in 1966. I obtained a diploma of engineer in Electrotechnics in 1992. He received his master Department of Electrical Engineering at the ENSET, in Oran, Algeria. He received “Doctorat Es-Science” in Electrical Control from the University of Sciences and Technology of Oran (Algeria) in 2014. He is an associate professor at university of Saida. His fields of interest include: FACTS power flow in radial distribution system and Renewable Energies. I am a member in electro technical engineering Laboratory (L.G.E)). Post address:Yahiaoui Merzoug , lecturer, University of Saida, BP 138 En-Nasr, (20000 Saida) , ALGERIA Email: myahiaoui2001@yahoo.fr |
| --- | --- |
|  | Bouanane Abdelkrim is born in SAIDA, Algeria in 1970 he obtained a diploma of engineer in Electrotechnics in 1995.I received my Master in 2006 at the ENSET Oran and PHD at the ENPO oran in 2013. I am a teatcher in the Department of Electrical Engineering, Faculty of Technology at the Dr. Moulay Taher University of SAIDA. My research interests include intelligent control of power system and FACTS, Electrical Machines and Renewable Energies.I am a member in electrotechnical engineering Laboratory (L.G.E)) |
|  | Larbi Boumediene is born in Saida (Algeria) in 1964. He obtained a diploma of engineer in Electrotechnics in 1990. He received his master Department of Electrical Engineering at the ENSET, in Oran, Algeria. He received “Doctorat Es-Science” in Electrical Control from the University of Sciences and Technology of Oran (Algeria) in 2007. He is an associate professor at university of Saida. His fields of interest include: harmonic power flow in distribution system, quality of energy. Post address: Larbi Boumediene, lecturer, University of Saida, BP 138 En-Nasr, (20000 Saida) , ALGERIA Email: lboumediene2005@yahoo.fr |