Feasibility and Optimal Design of Grid-connected Small Hydropower-Solar PV-Diesel Hybrid Power System for Rural Electrification

Bankole Adebanji1, Gafaru Abiola Adepoju2, Paul Olulope3, TaiwoFasina3, Olawumi.Adetan4

1, 2, 3, 4Department of Electrical and Electronic Engineering, Ekiti State University, Ado-Ekiti, Nigeria

| Article Info |  | ABSTRACT |
| --- | --- | --- |
| Article history: Received April, 2020 Revised , 2020 Accepted , 2020 |  | The need for hybrid design to be optimal in terms of operation and component selection serves as a constraint in obtaining reliable electricity at a minimum cost. This work carried out the feasibility of installing a Small Hydropower (SHP) into an existing water supply dam and development of an optimal sizing optimization model for a typical Nigerian village-Itapaji. The Hybrid Power System (HPS) model developed in this work consists of Photovoltaic (PV) system, SHP generator, Battery (BATT) bank and Diesel Generator (DG). The optimal sizing of the system’s components for optimum configuration was carried out using Genetic Algorithm. This was done for three types of hybrid systems: PV-BATT-DG, SHP-PV-BATT-DG and Pumped hydro-PV-BATT-DG. The hybrid model’s results were compared with Hybrid Optimization Model for Electric Renewable (HOMER) using correlation coefficient (r) and Root Mean Square Error (RMSE) to verify its validity. The stability impacts of the SHP and PV on the existing distribution network were also investigated using DIgSILENT power factory software.The results of the simulation obtained from the developed model showed better correlation coefficient (r) of 0.88 and Root Mean Square Error (RMSE) of 0.001 over that of HOMER. The results of simulation for the stability analysis showed that the SHP and the PV energy dynamics have no significant negative impact on the dynamic behaviour of the distribution network due to its low penetration level.. This will serve as a guide for power system engineers in feasibility assessment and optimal design of HPS for rural electrification. . |
| Keywords: Hybrid Power System Optimal Sizing Genetic Algorithmn DigSILENT power factory Rural Electrification |  |  |
|  |  | This is an open access article under the CC BY-SA license. |
| Corresponding Author: B.Adebanji, Department of Electrical and Electronic Engineering, Ekiti State University, P.M.B.5363, Ado-Ekiti, Nigeria. Email:bankole.adebanji@eksu.edu.ng |  |  |

- INTRODUCTION

Renewable Energy Sources (RES) are now accepted globally to be the most effective solution in reducing global warming [1, 2]. There is no single energy generating system (composing of RES alone) that is reliable and cost-effective due to its fluctuating nature. A hybrid system of RES optimally combined with other conventional energy resources like Diesel Generator (DG) will serve as a better alternative [3].

Nigeria is naturally blessed with abundant RES which can be used for effective and rapid development of its rural areas. The abundant RES (high solar irradiance, wind speeds, high stream flows of rivers and abundant biomass) in these areas can be harnessed to form a hybrid system for a reliable and sustainable power supply at reduced cost. However, the need for hybrid design to be optimal in terms of operation and component selection serves as a constraint in obtaining reliable electricity at a minimum cost. Most of the available Hybrid Power System (HPS) models are very expensive, complex and not easily adaptable to suit local conditions for rural electrification [4, 5, 6, 7].

A study to identify the best solution for a recycled paper mill located in Rio Grande do soul, Southern Brazil for peak hours (19-22 hours) was conducted by [8].  The method considered the cost at peak hours only, the reliability was not considered. A general framework was developed for optimizing a hybrid system consisting of hydro, PV and wind energy sources using linear programming by [9]. Recommendations were also made on integration of RES into the Ghananian energy mix. Somano and Shunki (2017) [10] developed a hybrid model consisting of SHP and PV generators. The different combinations were analyzed for cost-effectiveness. The usage of DG or biomass was not considered as an alternative supply in case of non-availability of RES at a particular time.

A critical appraisal of the related  works and existing hybrid analytical softwares  showed that most of the works/studies on HPS have been designed to simulate and/or optimize  PV, wind, DG, e.t.c. Very few of the software-based models (except HOGA and HOMER) have provisions for small hydroelectric energy component. Some of the methods discussed were not able to find best compromise between reliability and system cost [11].

This work considered the feasibility of integrating Small Hydro Power (SHP) plants into an existing water supply dam and the development of a Small Hydro-PV-DG HPS model for feasibility assessment and optimal sizing of Hybrid renewable energy system in rural areas. The stability impacts of the SHP and PV on the existing distribution network were also investigated using DIgSILENT power factory software [12]. Ele River, Itapaji Ekiti, Nigeria was selected to be to be used as a case study for rural electrification.

The work is divided into four sections. The work was introduced in section one, followed by the methodology used in achieveing the research objectives. The results were presented and discussed in section three. The work was concluded with recommendations for future research in section four.

2. METHODOLOGY

This session presents each research objective and outlines the key steps taken to achieve them. The details on input data, collection method and steps taken in data analysis including all the assumptions and limitations were discussed in the subsequent sub-sections.

2.1 Data Acquisition and Description of the Study Area

Data for water supply and demand were obtained from Ekiti State Water Corporation, Ado-Ekiti. Reservoir capacity, river head, flows gauge heights, stream flow rate and climate data were obtained from Benin-Owena River Basin Development Authority (BORDA) Benin-city and Akure Airport Meteorological station, Nigeria [13, 14].The information about the lines, loads and transformers were obtained from the utility distribution company, Benin Electricity Distribution Company (BEDC), Ado-Ekiti.The study area selected for this work is Ele river water supply dam, Itapaji-Ekiti, Nigeria. It is on longitude 5o.12 E and latitude 7o.38 N. Total annual rainfall ranges between 1350-1400 mm, while temperature ranges between 32 oC-35 oC (dry season) and 21 oC-22 oC (wet season) [15].

2.2    Feasibility study of SHP Integration and RES Evaluation

The feasiblility study was carried out in order to make unbiased technical hydrological decision on the viability of the dam. The approach adopted was to create a suitable head with a combination of a sustainable high flow rates with steep gradients for SHP generation. Since the dam was already being used for water supply, the head and stream flow was adopted. The Flow Duration Curve (FDC)-hydrograph with daily data was compiled for the past thirty years [16].

# 2.3 Mathematical Models of the HPS Components

. The steps to achieve the modeling of each hybrid component are as outlined in the following sub-sections.

(a)  Small hydropower (SHP) Generator

The electrical power output of the SHP unit is given as in (1) [17]

| Nomenclature |  |  |  |
| --- | --- | --- | --- |
| PSHP | Power output of the turbine |  | Battery bank voltage |
| Hnet | Effective head |  | Maximum battery Depth of Discharge |
|  | Density of water (1000 kg/m3) |  | Battery efficiency |
| G | Acceleration due to gravity (9.8 m/s) |  | Battery autonomy or storage days |
| Q | Water discharge expected to pass through the turbine (m3/s) | kT | Temp coefficient of maximum power |
|  | Output power from the PV cell | Tref | Cell temperature @reference conditions |
|  | Rated power at reference conditions | Vbus | Voltage of the bus when connected |
|  | Solar radiation (1000W/m2) at reference conditions (25oC) | C(t-1) | Battery capacity at previous increment |
|  | Cell temperature | EDG | Total energy of oil |
|  | Solar insolation in kW/m2 | Cfuel | Fuel cost |
|  | Annualized capital cost of each of the component | Cdiesel | Fuel price per litre |
|  | Annual operation and maintenance cost | PBATT | Battery capacity |
|  | Annual fuel cost | SOCmin | Minimum State Of Charge |
|  | Annual value of replacing expenditure of components during the project lifetime | SOCmax | Maximum State Of Charge |
|  | Annual emission cost generated from DG | NSHP | Number of Hydro turbine |

(1)

(b)  Photovoltaic (PV) model

The maximum power output from the PV cell can be calculated as in (2) [18, 19, 20].

(2)

(c) Battery bank model

Koutroulis et al, (2006) [21] calculated the capacity of the battery at a point in time t, as follows in (3).

(3)

is as in (4)             [21].

(4)

The value is positive when the battery is charging.

(d) Diesel Generator (DG) model

The diesel generator is an energy conversion system from fuel to electricity with a conversion efficiency of,  so that it can be described by (5) [19].

(5)

A linear model has been assumed for the fuel consumption rate (F) in litres/hour of operation by the DG [19] given in (6).

(6)

The fuel cost,  can be calculated using the formula as in (7)

(7)

2.4 Development and Validation of the HPS model

A small hydro power-based HPS model to determine an optimal configuration with minimum cost and of high reliability was developed in this section. It is assumed that the HPS will work continuously for twenty four hours and that the electrical load and the RES are constant within one-hour time step.

The objective function here is an economic function that is constrained in a technical or reliability function. The problem was modeled according to the Loss of Power Supply Probability (LPSP) and total Annualised Cost System (ACS).  The decision variables for the problems are taken as number of hydro turbines, number of Solar PV panels,  number of battery banks and the capacity of the generator unit because these variables affect the cost and LPSP, which can change  [22].

The ACS is as given in equation (8) [23, 24 ,25] while the LPSP [26, 27,28] is as expressed in equation (9)

(8)

[28]                                                          (9)

This is subject to an inequality constraint equation (10)

[27]                                                                            (10)

Reliability evaluation are carried out in the worst conditions as given in equation (11)

(11)

In order to solve the optimization problem, all the constraints subsequently presented must be satisfied [24, 29]

(12)

SOCmin≤SOC(t)≤SOCmax       (Battery capacity constraint)                                                       (13)

0≤NPV,P≤NPV,Pmax                  (Non-Negative Constraints)                                                       (14)

0≤NSHP≤NSPV max                                                                                                                       (15)

0≤NBAT,  P≤NBAT,Pmax                                                                                                                  (16)

The power outputs from the SHP turbine were calculated using power equation (1) taking the average stream flows as input. The power outputs from the PV-arrays were calculated at an hourly basis from the power equation (2) using the hourly solar irradiance values as the input. The RES were added together and compared with the hourly load demand. The battery bank and the DG operate depending on whether the total RES is equal, less or more than the load demand. The flowchart diagram for this simulation is as shown in Figure 2.

Genetic Algorithm (GA) was utilized in this simulation to determine the optimal configuration The best chromosome in the final generation is considered as the optimum parameters value of the hybrid system. GA based MATLAB m-file code was developed to determine the optimal configuration of Small hydro-Photovoltaic-Diesel hybrid system of the case study [30].

The HPS model was validated by comparing its results with HOMER [31] as a benchmark [15].  The simulation was done in MATLAB/Simulink environment. The data published by Ani and Nzeako (2013) [32] were used as the validating data. Coefficient of correlation (r) and Root Mean Square Error (RMSE) were used to measure the performance of the two models. The new model was then applied to the case study area to evaluate its performance.

2.5 Modeling and Simulations of the Existing Distribution Network with RES Integration

In order to assess the impact of integrating Solar PV-Small Hydro Power on the existing distribution network, DIgSILENT simulation software version 15.2 was used. A frequency limit of 500.05 and nominal voltages of 33 kV and 11 kV 6% were used. The single line diagram of the distribution network is shown in Figure 3. It consists of one (15 MVA), 11/0.415 kV power transformer, two (630 kVA) 0.415/11 kV transformers and three (250 kVA), 11/0.415 distribution transformers.  The total load considered for the network is  kW + j1000 kVar. Modeling and simulation of the existing distribution network along with a comprehensive dynamic stability analysis with RES integration were carried out. The solar PV was integrated into the existing distribution network as a DC source through a Pulse Width Modulation (PWM) inverter and the SHP through a Synchronous Generator (SG) [15]. Dynamic stability analysis was carried out with RES integration.  A three phase short circuit fault was applied at bus 5 (line 4) and cleared in 0.02 seconds by removing the line.

3. RESULTS AND DISCUSSION

  - Feasibility study for Small hydropower plant Integration

It was observed that during the raining season (April-October) there were enough hydro sources to run the turbine. The stream flow reaches its peak of 15,500 L/S in September.  The hydro power potential is to generate 2.70 MW at maximum discharge of 23.24 m3/s., 966 kW at average annual discharge of 8.33 m3/s. and generate 206.5 kW at minimum discharge of 1.78 m3/s during dry season with a reservoir capacity balance of 0.124109 m3/year.    The estimated power demand for the village as at September, 2019 is 621 kW. The demand forecast for year 2028 is 1210 kW.

The hydro turbines generate 206.5 kW at minimum discharge during dry season. The power deficit is 414.5 (621-206.5) kW.  621-206.5kW=414.5 kW   Consequently, there is need to complement the hydro power source with another renewable energy-Solar PV. Hence, the need for small hydro power plant based hybrid system.

  - HPS Model validation results

The optimal sizing results for both HOMER and the developed model is shown in Table 1. The simulated results obtained from HOMER showed a good correlation (correlation coefficient (r) is 0.88 while the Root Mean Square Error (RMSE) is 0.001) with those obtained from the developed model.  The little difference in the results is due to the different modeling approaches adopted in the modeling of the generators. However, these do not have significant effect on the overall results. Generally, the modeling of the component generators in MATLAB/Simulink was comparable to those obtained using HOMER. .

The developed model gives higher priority to the hydro turbine than the solar panel due to the higher cost of solar panel. This is especially more economical when a dam-based SHP is used. The developed model is simple, more reliable and can easily be modified according to the need of a particular project.

Table 1: Validation results

| Description | HOMER | Developed model |
| --- | --- | --- |
| SHP (kW ) | 10.7 | 11 |
| PV panel (kW) | 10.3 | 10 |
| DG (kW ) | 16 | 16 |
| BATT (kWhr) | 6.9 | 7 |
| R.F. (%) | 0.68 | 0.70 |
| COE ($/kWhr ) | 0.267 | 0.268 |
| LPSP | 0.0054 | 0.0045 |

Figure 2: Flowchart of the Hybrid Power System model

Figure 3: Single Line Distribution Network of the Study Area

3.3: Optimal sizing results for the study area-Itapaji Ekiti

The results of the different combinations at peak load demand are as presented in Table 2 while the average monthly electric  power production for the three hybrid combinations were as presented in Figures 4,5 and 6.

Table 2: Optimal sizing result for the three Hybrid combinations at Peak load demand.

| Component | Solar PV-BATT-DG System | SHP-BATT-DG System | Pumped hydro-Solar PV-BATT-DG System |
| --- | --- | --- | --- |
| Pumped hydro (kW) | - | - | 960 |
| SHP (kW) |  | 960 | - |
| Solar PV (kW) | 640 | 320 | 64 |
| DG (kW) | 400 | 200 | 0 |
| BATT (kWhr) | 1000 | 1000 | 0 |
| COE ($/kWhr) | 0.309 | 0.187 | 0.068 |
| RF (%) | 0.38 | 0.81 | 0.98 |
| LPSP | 0.0004 | 0.0004 | 0.0001 |
| ACS ($) | 785,400 | 675,860 | 43,313 |
| Operating cost ($) | 44,985 | 24,774 | 12,572 |

Figure 4: Monthly average electric production for the Solar PV-BATT-DG Hybrid system at peak load demand.

Figure 5: Monthly average electric production for the SHP-Solar PV-BATT-DG Hybrid system at peak load demand.

Figure 6: Monthly average electric production for the Pumped hydro-Solar PV-BATT-DG Hybrid system at peak load demand.

(a) Solar PV-BATT-DG Hybrid combination

The PV contributed 1,666,076 kWhr per year while the DG contributed 1,034,304 kWhr per year. The DG consumed $451,687 litres per annum. The COE at peak load and low load demand was 0.309. The solar PV and DG sizing values are very high compared to when the SHP and pumped hydro systems were used. It can be seen from Figure 4 that the hybrid systems made use of both the Solar PV and the DG in the year. The hybrid system made less use of the DG during the dry season (October-March) when there is high Solar irradiation and made much use of the DG during the raining season (April-September) when there is less Solar irradiation.This accounted for a very high operating cost. The COE was higher than any other combinations considered in this work. The cost may be too high for the rural dwellers.

(b) SHP-PV-BATT-DG Hybrid combination

The hydro turbine contributed 3,023,323 kWhr per year; PV contributed 726,065 kWhr per year contributed while the DG contributed 524,634 kWhr per year. The DG consumed $233,091 litres per annum. The PV and the DG sizing values reduced accordingly. This is because of the high SHP sizing value which has lower annualized cost than other hybrid components. It can be seen from Figure 5 that the hybrid systems made use of DG during the months of November-April (dry season with relatively low stream flow). This accounted for an increase in the cost of production due to high cost of diesel. However, between May and October ((raining season with relatively high stream flow) there were enough hydro sources to turn the turbine.

(c) Pumped hydro-PV-BATT-DG Hybrid combination

The pumped hydro contributed 5,749,422 kWhr per year and the PV contributed 13,375 kWhr per year. The Pumped hydro- PV-BATT-DG hybrid system showed a better improvement in terms of annualized cost, COE, RF and operating cost. It can be observed from Table 2 that the DG and the BATT made no contribution to the electricity production. This is because the pumped hydro system produced a constant supply throughout the year. This is due to the fact that the pumped water were used and recycled. During low load demand, the water is pumped and stored in the storage system but when there is peak demand, the water is used to meet the demand. Thus, this brings the operating cost to be very low and thus lessens the environmental effects. The cost of generating the hydro is the least when compared with solar PV and DG. The COE for both the peak and low load demand scenarios was 0.068 (with RF of 0.98). This will indeed be more affordable to the rural dwellers.

3.4: Steady State Simulation Results with RES integration

The steady state simulation results showing the active power (MW), reactive power (Mvar) and voltage (p.u.) were shown in Figures 7-9. It is shown in Figure 7 that that the active powers of all the integrations are the same. This is possible because the penetration level of the renewable energy is low and that the single generator has capacity to supply the small load connected to the grid.

The reactive power (Figure 8) when there is no integration of the renewable energy (only the generator supplies the load) is very different from the rest of the simulations. This is because the grid is limited in reactive power and the single generator has to supply the reactive power to keep the grid voltage stabilized. However, when renewable energies are connected especially SHP, it supplies reactive power to the grid thereby stabilizing the network the more. The effect of the low reactive power will be more, if the penetration level is high. It indicates that the village will be better supplied if the renewable energy is adequately integrated into the grid resulting into stability of the entire network.

It can be observed from Figure 9 that the voltage of the system remains constant even with the integration of the RES. It should be noted that the  PV contributed no reactive power into the system because of its relatively low inertia as a results of its stochastic characteristics.

3.5: Dynamic stability simulation results with RES Integration

The Dynamic stability simulation results with RES Integration showing the active power (MW), reactive power (Mvar) and voltage (p.u.) were shown in Figures 10-12

Figure 7:  Active power (MW) for the existing distribution network with and without RES integration

Figure 8:  Reactive power (Mvar) for the existing distribution network with and without RES integration

Figure 9: Voltage (p.u.) for the existing distribution network with and without RES integration

Figure 10: Active power (MW) for the existing distribution network with and without RES integration

Figure 11: Reactive power (Mvar) for the existing distribution network with and without RES integration

Figure 12: Voltage (p.u.) for the existing distribution network with and without RES integration

The active power (MW) with renewable and without renewable are almost the same because of the low penetration level. In case of higher penetration, especially PV, it will introduce more instability into the system. The reactive power reaches its maximum swing of 0.135 and stabilizes very quickly with lower generation of reactive power. The result showed that RES can be used to produce reactive power especially; the SHP.

4. CONCLUSION AND RECOMMENDATIONS

This work considered the feasibility of integrating SHP plants into an existing water supply dam and the development of a SHP-PV-DG HPS model for feasibility assessment and optimal sizing of Hybrid renewable energy system in rural areas.  The hybrid model’s results were compared with those obtained from HOMER to verify its validity. The developed model simulation results were favourably comparable and very close to those obtained using HOMER. Optimal sizing of the system’s components for optimum configuration was done using Genetic Algorithm. The results showed that the Pumped hydro-Solar PV-BATT-DG hybrid system was the best of all the hybrid combinations considered in this work in terms of COE and RF. The objective of the work is to achieve an efficient and cost-effective system configuration so that the HPS could improve the quality of life of the rural dwellers.

The work also analyzed the impacts of integration of some renewable energy generators (Small hydropower and Solar PV) on a typical Nigerian distribution network in the study area. Static and dynamic models of the distribution network with /without RES integration were developed using DigSILENT standard library models. The results obtained showed that the steady state voltage magnitude is maintained within acceptable range and that the system’s components are not heavily loaded. The Nigerian government should as a matter of urgency integrate the available RES into current energy mix to improve power generation in the country.

Acknowledgements

This research work was made possible through the enabling research environment provided by the Ekiti State University, Ado-Ekiti, Nigeria and Ladoke Akintola University of Technology, Ogbomosho, Nigeria. The authors expressed their gratitude to all the staff and students of these institutions for their invaluable contributions.

REFERENCES

[1] G.A.Adepoju and B. Adebanji, “Feasibility and  Optimal Design of Small Hydropower-Solar Photovoltaic-Diesel Generator Hybrid System for Itapaji-Ekiti State, Nigeria” Science Domain International, Journal of Scientific Research and Reports,Vol.11, pp.1-10, 2016.

[2] A.Hepbasli, “A key Review on Exergetic Analysis and Assessment of Renewable Energy sources for a sustainable future” Energy Reviews,Vol.2,pp..593-661, 2008.

[3] S.K.Ramoji and B.J.Kumar, “Optimal Economical Sizing of a PV-Wind Hybrid Energy System using Genetic Algorithm and Teaching Learning Based Optimization” International Journal of Avanced Research in Electrical,Electronics and Instrumentation Engineering,Vol.2, pp..34-56,2014.

[4] H.Hildebrand, ”Planning Tool for small Hydropower Development” presented at the Technical University of Georgia in Tbilis on behalf of UNESCO at the International Hydropower Association. pp.23-57,1997.

[5] T.Honerica and H.Tawanda, “A Technical Model for Optimizing PV/Diesel/Battery Hybrid Power Systems” CSIR Proceedings Science real and Relevant Conference, pp.23-34,2010.

[6] S.Hossein and M.Farshid, “Feasibility and Optimal Reliable Design of Renewable Hybrid Energy System for Rural Electrification in Iran” International Journal of Renewable Energy Research,Vol.2 ,pp.:574-581,2012.

[7] B.Adebanji., G.A.Adepoju , O.O. Fagbohun  and  P.K. Olulope, “Development of Simulation and Optimization model for rural Electrification” Science Domain International, Journal of Scientific Research and Reports,Vol.15, pp.1-13,2017.

[8] A.Beluco, C.P. Colvara, I.E.Texeira and A. Beluco, “Feasibility Study for Power Generation during Peak Hours with a Hybrid System in a Recycled Paper Mill”Computational Water, Energy and Environmental Engineering, Vol.2,pp.:45-53,2013.

[9] A.Acakpovi, “Original Framework for Optimizing Hybrid Energy Supply”Journal of Energy.Vol.2, pp.1-10, 2016.

# [10] G.Z. Somano and G.Shunki, “Design and Modeling of Hybrid PV-Micro Hydro Power Generation case study Jimma zone” American Journal of Electrical Power and Energy System, Vol.2,pp.43-48,2017.

# [11] T.R.Ayodele.and A.S.O. Ogunjuyigbe, “Mathemathical Methods and Software Tools for Designing and Economic Analysis for Hybrid Energy Systems” International Journal of Renewable Energy,Vol. 9 pp.:57-68,2014.

# [12] DIgSILENT, “DIgSILENT Power Factory 14.1: Software Manual, Vol. 1,2011..

[13] BORDA, “Benin-Owena River Basin Development Authority”. Hydrological Year  Book,pp.2,2011

[14] FMWR “Pre-Feasibility Report on SHP projects” Federal Ministry of Water Resources-Benin-Owena River Basin Development Authority.pp.1-54, 2007.

[15] B.Adebanji,”Development of a Hybrid Power System Model For Rural Electrification” an unpublished Ph.D thesis Submitted to the Department of Electronic and Electrical Engineering, Ladoke Akintola University of Technology,Ogbomoso,Nigeria,2019.

[16] A. Angstrom, Solar and Terrestrial Radiation. Retrieved from www.arpapress.com

[17] D.S.Ashok, Optimized Model for Community-based Hybrid Energy System; Renewable Energy,Vol.2,pp.1155-1164,2007

[18]  A.K. Dauid  et.al., “Simulation of a Hybrid Power System consisting of Wind Turbine, PV, Storage Battery and Diesel Generator; Design, Optimization and Economical Evaluation” International Journal of Energy Engineering,  pp.56-61,2011.

[19] A.Vahabzadeh, et.al.,”Optimal Sizing of Hybrid Energy resources for Electricity Distant Rural areas of Iran” Paper no. 03222 CIRD Workshop-Lisbon. pp. 29-30,2007

[20] M.Jariso et.al.,  “Modelling and Designing of Stand-alone Photovoltaic System (Case Study: Addis Boder Health Center South West Ethiopia)”, IEEE International conference on Electronics, communication, and aerospace Technology,  pp. 168-173,  April, 2017.

[21] Koutroulis, E., Kolokosa, D., Potirakis, A., and kalaitzakis, K. (2006). Methodology for Optimal sizing of stand-alone Photovoltaic/Wind-Generator Systems using Genetic Algorithms; Solar Energy 80(2): 1072–1088.

[22] B.Adebanji et.al,, “Optimal Sizing of an Independent  Hybrid Small Hydro-Photovoltaic–Battery-Diesel Generator Hybrid Power System for a Distant Village.” International Journal of Scientific and Technology Research Vol.6, Issue 8, pp.208-213,2017.

[23] O.Skarstein and K.Ulhen,“Design Considerations with respect to long term Diesel saving in Wind/Diesel Plants” Wind Engineering, Vol.13pp.136-142, 1989

# [24] P. Suhane, S. Rangneker and A.Mittel, “Optimal sizing of hybrid energy system using Ant Colony Optimization” International Journal of Renewable Energy Research, Vol.4,pp.683-688, .2014.

[25] Y.Hungxing, “Optimal Sizing Method for Stand-Alone Hybrid Solar-Wind System with LPSP   Technology by using Genetic Algorithm” Solar Energy, Vol. 82,pp. 354-367, 2008..

[26] S.C. Gupta, Y. Kumar and G Agnihotri, “Renewable Energy Analysis and Sizing Tool (REAST)” Journal of Electrical Systems Vol. 7,pp..206-224,  2011.

[27] S.C.Gupta, K. Kumar and G.Agnihotri, “Optimal sizing of Solar-Wind hybrid system in Information and Technology in Electrical sciences “ ICTES IET-UK International conferences pp.282-287, 2011.

[28] J.A.Gupta,K.P.Saini and M.P. Sharma, “Modeling of Hybrid Energy System Part I- Problem Formulation and Model Development, Part II-Combined Dispatch Strategies-Part III-Case Study with Simulation Results” Renewable Energy Vol.36,pp.459-481, 2011.

[29] P. Suhane., S. Rangneker and A. Mittel,“Optimal sizing of hybrid energy system using Ant Colony Optimization” International Journal of Renewable Energy Research, Vol.4 , pp.683-688,2014.

[30]MATLAB/Simulink, www.mathworks.com/access/helpdesk/help/toolbox/physmod/powersys/simplifiedsychro

# [31] HOMER, (2009). The Micropower Optimization Model , Homer,Enegy” Version 268 beta www.homerenergy.com.

[32] V.A. Ani,and A.N. Nseako, “Potentials of Optimized Hybrid System in Powering Off-Grid Macro Base Transmitter Station Site; International Journal of Renewable Energy Research, Vol.3,pp.861-871, 2013.

Appendix 1: Detailed parameters of the components [1, 14]

| Solar PV Specifications |  | SHP Parameters |  |
| --- | --- | --- | --- |
| Module Type | RNG 160P | Nominal Power (kW) | 96 |
|  | 160 | Available Head | 21.6 |
|  | 22.8 | Design flow rate | 4.33 m3/s |
|  | 9.47 | Turbine efficiency | 75% |
| Module efficiency | 14.05% | Life time | 25 years |
| Dimension |  | DG Parameters |  |
| NOCT | 46OC | Size | 200 kW |
|  | 18.6 | Quantity | 2 |
|  | 8.6 | Lifetime | 20,000 hrs |
| Life time | 25 years | Price | 0.884 $/litre |
| Battery Specifications |  | Converter details |  |
| Minimum lifetime | 4 years |  |  |
| Initial State of Charge (SOC) | 100% | Size | 791 kW |
| Depth of Discharge (DOD) | 80% | Life time | 15 years |
| Voltage | 12 V | Inverter efficiency | 90% |
| Efficiency | 80% | Rectifier efficieny | 85% |

APPENDIX 2 - Detailed Cost parameters of the components (Initial, Replacement and Maintenance costs)

| Component | Initial cost | Replacement cost | Operation & Maintenance cost |
| --- | --- | --- | --- |
| Solar PV modules | 2500 $/Kw | 2500 $/kW | $5 |
| Hydro Turbine | $430,247 | $430,247 | $10,308 |
| Diesel Generator | 503.08 $/kW | 503.08 $/kW | 15 $/hr |
| Battery | 1710 $/kAh | 1710 $/kAh | 76 $/kAh |
| Converter | $8043 | $8043 | $0 |

Appendix 3:  Line data of the Existing distribution system

| Transformers’ types and ratings |  |  | Load lines and cable lengths |  |  |
| --- | --- | --- | --- | --- | --- |
| Transformer | Ratings |  | Line | Lengths(m0 | Line parameters |
| T1 | 30 MVA,33/11 kV,0.0485+j0.0545 |  | L1 | 500 | 0.266+j0.942 |
| T2 | 250 kVA,11/0.415,0.00385+0.0087 |  | L2 | 300 | 0.266+j0.941 |
| T3 | 250 kVA,11/0.415,0.00385+0.0087 |  | L3 | 500 | 0.266+j0.941 |
| T4 | 250 kVA,11/0.415,0.00385+0.0087 |  | L4 | 600 | 0.266+j0.941 |
|  |  |  | L5 | 600 | 0.266+j0.942 |
| Technical characteristics of 11/0.415 kV cables |  |  |  |  |  |
| Cable type |  |  |  |  |  |
| 11 Kv |  | 0.545 |  | 0.414 |  |
| 0.415 Kv |  | 0.568 |  | 0.075 |  |

BIOGRAPHIES OF AUTHORS (10 PT)

| Bankole Adebanji | Bankole Adebanji received the B.Eng.degree in Electrical and Electronic Engineering in 1997 from the then Ondo State University, Ado-Ekiti, Ekiti State, Nigeria (now Ekiti State University, Ado-Ekiti ), M.Tech.degree (Electronic and Electrical Engineering) and Ph.D degree ( Power System Engineering and Machine) from Ladoke Akintola University of Technology (LAUTECH), Ogbomoso, Nigeria in 2010 and 2019 respectively. His researh interest are Renewable energy,Power system engineering,Hybrid,Small hydro and optimization.He is a resgistered COREN Engineer and a member of Nigerian Society of Engineers (MNSE). He is currently lecturing in the Electrical and Electronic Engineering department of Ekiti State University, Ado-Ekiti, Nigeria. |
| --- | --- |
| Gafari Abiola Adepoju | Adepoju Gafari A. received the degree of B.Tech. in Electronic and Electrical Engineering from the Ladoke Akintola University of Technology, Ogbomoso in 1997; M.Sc. degree from University of Lagos and Ph.D. from Ladoke Akintola University of Technology, Ogbomoso in 1999 and 2011 respectively. He is currently Professor of power system Engineering in the Department of Electronic and Electrical Engineering, Ladoke Akintola University of Technology, Ogbomoso. His research interests are: power system Engineering and Machines; Power Electronic Converters and Electric Drives; and Renewable Energy Engineering. |
| Paul Kehinde Olulope | Olulope P.K had been a University lecturer since June 2002 till date at the Ekiti State University, Nigeria. He completed his Doctoral degree in Power System Engineering from the University of Cape Town, South Africa. He completed his Master degree program (M.Eng.) in Electrical and Electronic Engineering from the University of Benin, Edo State, Nigeria and Bachelor of Engineering (B.Eng) at Ekiti State University in 2005 and 2002 respectively . He is a registered member of the Institute of Electrical and Electronics Engineers (IEEE), a registered member of the Council for the Regulation of Engineering in Nigeria (COREN) and the Nigeria Society of Engineers (NSE).His Research interest is on the application of Computational intelligence to power system, integration of renewable energy and distributed generation into power grid. |
| Taiwo Fasina | Fasina E.T. received B. Eng. from Ekiti State University Ado Ekiti, Nigeria in 1998 and M. Tech. from Ladoke Akintola University, Ogbomoso, Nigeria in 2012. He did his Ph.D. from Cardiff University, UK in 2019. He is currently a lecturer in Ekiti State University, Ado Ekiti, Nigeria. His main interest includes power system analysis, distributed generation, localised energy systems, deregulation and electricity transmission pricing. |
| Oluwumi Adetan | Oluwumi Adetan holds a Bachelor of Engineering (B.Eng.) degree in Electrical and Electronic Engineering from the then Ondo State University, Ado-Ekiti, Nigeria (Now Ekiti State University, Nigeria), a Master of Engineering (M.Eng.) degree in Electrical and Electronic Engineering (Communication Option) from the Federal University of Technology, Akure, Nigeria. He completed in 2014 his Doctoral degree in Electronic Engineering from the University of KwaZulu-Natal, South Africa. His research interests are on radio wave propagation and to study the effects of rain on microwave propagation and wireless communications systems. He is a registered member of the Council for the Regulation of Engineering in Nigeria (COREN). He is currently a Senior Lecturer in the Department of Electrical and Electronic Engineering, Ekiti State University, Nigeria. |