| Laboratory investigation of the impact of air pollution on partial Discharge inception voltage of insulators in a specific region y.shafiei1. F.Faghihi2. H.Heydari3. A.H. Salemi4 1,4 Department of Electrical Engineering, Islamic Azad University, Arak, Iran 2 Science and Research Branch, Islamic Azad University, Tehran, Iran 3 Department of Electrical Engineering, University of Science and Technology of Iran, Tehran, Iran |  |  |
| --- | --- | --- |
| Article Info | Abstract Studying The discharge characteristics of transmission line insulators in the presence of pollution, particularly when The contaminated layer is wet by rain, fog or condensation, is necessary for selecting the proper insulation. Therefore, identifying the major air pollutants as well as the most effective ones on the discharge performance of outdoor insulators is mandatory. A systematic approach has been proposed to evaluate the impact of dominant air pollutants of an area on partial discharge (P.D) inception voltage of specimen insulators. Based on the suggested method, determining the pollution constituents, defining the dominant pollutant of the area, finding The most commonly used insulators for medium and above distribution voltages within The geographical boundaries of the central province of Iran, as well as examining The effect of dominant air pollutant of the region on partial discharge inception voltage of designated insulators by laboratory measurements, are The necessary steps toward a comprehensive study of the subject. |  |
| Key words: conductive layers inception voltage insulators, partial discharge(P.D) pollution |  |  |
| Corresponding Author: F.Faghihi Faculty of Electrical and Computer Science Research Branch, Islamic Azad University Email: Faramarz.Faghihi @srbiau.ac.ir |  |  |

1. Introduction

Based on the definition which has been presented in IEC 270[1], a partial discharge is an electric discharge that only partially bridges the insulation between conductors. Partial discharges often occur locally and are caused by an intensification of the electrical field and consequent air ionization on an insulator's polluted or damaged surface. Although this phenomenon releases not much energy, it will gradually develop and lead to flashover and break down the insulator. Even if the partial discharge does not end to flashover, it will degrade the insulator's dielectric property [2-3].

According to reliable statistics, a high percentage of service interruptions are caused by moisturized outdoor insulators' contamination. Nowadays, air pollution is a problem in industrial countries and developing areas of The world [4-5]. Air pollution constituents, in rain or fog conditions, cause the formation of a conductive layer which leads to flow of leakage current and discharges on transmission line insulators surfaces [6,7].

Several investigations for various air contaminants and in different parts of the world have been performed and reported in many articles in the literature[8-12]. Nevertheless, most of them have focused on examining one kind of air pollution constituent on selected specimens' discharge behavior.

Present work, however, is based on a detailed study of all major air pollutants of the area of interest and the probable impact of dominant and the most effective one on partial discharge inception voltage of commonly used insulators in a specific region[13]. Furthermore, a new systematic approach to the problem has been suggested and has been presented in a flowchart diagram in Figure1.

In This experiment, we only measured The partial discharge inception voltage, and other quantities such as The number of charges, discharge power, discharge current, etc, are not covered.

Determination of the pollution constituents for central province of Iran

Defining the dominant pollutant of the area

Finding the most commonly used Insulators for central province of Iran for distribution and medium voltages

Examining the effect of dominant pollutant of the region on partial discharge inception voltage of specimen Insulators

Tables of P.D Inception voltages for various conditions of designated insulators

Determination of the pollution constituents for central province of Iran

Defining the dominant pollutant of the area

Finding the most commonly used Insulators for central province of Iran for distribution and medium voltages

Examining the effect of dominant pollutant of the region on partial discharge inception voltage of specimen Insulators

Tables of P.D Inception voltages for various conditions of designated insulators

figure 1. flowchart of suggested method of investigation

2. Climate evaluation and Determining The dominant air pollution constituent.

According to the information from seven stationary stations and eight mobile measuring groups, suspended particle matters (spm), sulfur dioxide (So2), and carbon monoxide (Co) were the major air pollutants throughout the region. The measurement period was one year, from April to the end of March, 2017. The percentage of each, has been graphically shown in figure 2,

Figure 2.  percentage of (co) measured in different stations (24hours average)

Figure 3. and Figure 4. So2 and Co are in gas forms, and Their solubility in water is very limited. On the other hand, They hardly would be sedimented on the insulator surface.  Therefore, a mix of  (SPm)  and salty dust, originated from MIGHAN salt lake and its surrounding desert, which is located 5 km northeast of the biggest city of the province, identified as the dominant air pollutant for the district under study[14,15].

Consequently,  a  sample from the aforementioned mixture was gathered to be used as a substance for artificial pollution Tests.

Figure 3.  percentage of (SO2),measured in different stations (24hours average)

Figure 4.  percentage of (SPm),measured in different stations (24hours average)

3. Materials and methods: Test facilities, circuits, specimen and procedure.

Experimental investigations were performed in the laboratory of the science and Technology university of Iran (Center for High voltage Researches).  The power was supplied by a 100  KV,200KVA pollution test transformer (Figure 5). The test voltage shall comply with the requirements of IEC 60-1 [16], the AC pollution test requirements recommended by IEC standards 60507,60815 and partial discharge measurement requirements recommended by IEC 270 and, [17,18].

Figure 5. High voltage Source Transformer

Figure 6. Coupling Capacitors

Test circuit is shown in Figure7 (a,b,c,d and e). Where ''Ca'' is the test object, ''Zm'' is an impedance that connects in parallel with the measuring instrument. ''Z'' is an impedance that could be substituted by a 10 resistor to prevent discharge pulses from being by-passed  Through  The high voltage supply and to reduce interference from the source.

Figure 7(a). Actual Test circuit for (P.D) inception Voltage measurement

Figure 7(b). test circuit recommended by IEC 270

Figure 7 ( c).Picture of Test circuit in Lab                   Figure7(d). Picture of Test Circuit with the test object

Figure 7(e). Partial Discharge detector

The purpose of the test is to measure the inception voltage (Uf), according to subclasses 3.5.1 , IEC 270. Therefore, we gradually increased the voltage from a lower value at which no discharges are observed, till The lowest voltage (Uf), at which partial Discharges exceeding a specified intensity are observed.

Wetting time in order, for The Pollution layer, to be solved in water, should at least be 20 minutes in case of glass and porcelain insulator, and 30 minutes for composite-polymer insulators. however, in the above tests half an hour wetting time was considered for all insulators [19].

The specimens were The most commonly used types of insulators in transmission   lines   of   the   central   province   of   Iran.   Profiles, dimensions and basic parameters are shown in Figure.8 and Table 1.

Table1. parameters of tested insulators

| Type | Materials | H(mm) | D(mm) | L(mm) | Max.Tensile (Mechanical),KN |
| --- | --- | --- | --- | --- | --- |
| A | Porcelain | 146 | 255 | 295 | 70 |
| B | Glass | 146 | 254 | 292 | 70 |  |
| C | SIR | 480 | 98/73 | 670 | 70 |  |

Type: C

Figure 8. Profiles of tested insulators

Where D is the diameter, L is the creepage distance and H is the height of The insulators.

4. Results and Discussion

Following The standard procedure, P.D inception voltage of specimen insulators when They were dry and clean and polluted by the area's dominant air pollutant was measured. The test results in different pollution severity (PS), a different angle of rain, and different uniformity of pollution materials are shown in Tables 2,3, and 4. Which are mostly comparing with those existing in the literature [20-24].

The results of artificial pollution tests are slightly different from what the insulators will be exposed to, in field and service, but according to many types of research and experiences [25-27], The difference would at most be less Than 8%. So That, The results of lab tests are reliable for the design and selection of outdoor insulators in locations of interest [28-31].

Table2: Results of the tests on porcelain insulator (Type A)

| P.D inception Voltage | Type and severity of pollution and rain condition |  |
| --- | --- | --- |
| 25kv | Clean and dry |  |
| 25kv | Dry and polluted |  |
| 19kv | Uniform pollution | Medium PS, Vertical rain |
| 18kv | Non uniform pollution |  |
| 17kv | Uniform pollution | Heavy PS, Vertical rain |
| 16kv | Non uniform pollution |  |
| 18kv | Uniform pollution | Medium PS, rain with the angle of 45° |
| 17kv | Non uniform pollution |  |
| 16kv | Uniform pollution | Heavy PS, rain with angle of 45° |
| 15kv | Non uniform pollution |  |

Table3: Results of the tests on glass  insulator (Type B)

| P.D inception Voltage | Type and severity of pollution and rain condition |  |
| --- | --- | --- |
| 20kv | Clean and dry |  |
| 20kv | Dry and polluted |  |
| 19kv | Uniform pollution | Medium PS, Vertical rain |
| 17kv | Non uniform pollution |  |
| 16kv | Uniform pollution | Heavy PS, Vertical rain |
| 14kv | Non uniform pollution |  |
| 18kv | Uniform pollution | Medium PS, rain with the angle of 45° |
| 16kv | Non uniform pollution |  |
| 15kv | Uniform pollution | Heavy PS, rain with angle of 45° |
| 13kv | Non uniform pollution |  |

Table4: Results of the tests on polymeric insulator (Type C)

| P.D inception Voltage | Type and severity of pollution and rain condition |  |
| --- | --- | --- |
| 30kv | Clean and dry |  |
| 29kv | Dry and polluted |  |
| 26kv | Uniform pollution | Medium PS, Vertical rain |
| 24kv | Non uniform pollution |  |
| 23kv | Uniform pollution | Heavy PS, Vertical rain |
| 21kv | Non uniform pollution |  |
| 25kv | Uniform pollution | Medium PS, rain with the angle of 45° |
| 23kv | Non uniform pollution |  |
| 22kv | Uniform pollution | Heavy PS, rain with angle of 45° |
| 20kv | Non uniform pollution |  |

5. Conclusion

From The test results, The following conclusions can be presented:

Increasing The pollution severity will decrease The Partial Discharge (P.D) inception voltage.

P.D inception voltage will be affected by The wetness degree of the pollution layer. Therefore, The voltage was recorded after making sure that the layer was saturated by moisture.

Non uniformity of pollution layer has a significant impact on P.D inception voltage and generally will decrease it. If the ratio of the windward area of an Insulator’s surface to the Leeward area is W/L, Then a reduction of This ratio will reduce The inception voltage. Therefore, The abovementioned factor, should be taken into account in calculating The overall creepage distance and in the selection and designing of insulator string in windy and desert locations.

Narrowing  The rain angle from The vertical position will slightly increase The partial Discharge inception voltage, in other words vertical rain is preferred in regard to P.D inception voltage.

In general, polymeric insulators have higher (P.D) inception voltages and better discharge characteristics than the glass and porcelain insulators under pollution conditions.

5. ACKNOWLEDGEMENT

The authors wish to thank Mr. kourosh Apornak who assisted in conducting this work and the environmental protection office of central province of Iran for providing useful information

References

[1]	International Electrotechnical commission (IEC) standard 270, "Partial Discharge Measurement,"   Geneva, Switzerland; IEC press; 2008.

[2]	D. Adhi, DM. Hepburn, BG. Stwart. "Comparison of partial Discharge characteristics and

degradation in several polymeric insulators," IET Science, measurement and Technology. Vol.6,

No.6, PP.474-484,2012.

[3]	V. Padma, V. raghavan, "Analysis of insulation degradation in insulators using partial

Discharge Analysis," IEEE 3rd international conference on Electronic & computer Technology

(ICECT), Vol4,PP.110-114,2013.

[4]	MA . Abouelsaad, MA. Abouelatta, B.  Arafa, ME. Ibrahim, "Environmental  Pollution effects

on insulators of northern Egypt, HV transmission lines," Proceeding of IEEE conference on

Electrical Insulation and Dielectric phenomena, Shenzhen, China, PP.35-38, 2013

[5]	R . Castillo- Sierra, O. Oviedo- Trespalacios, JE. Candela, JD. Soto, "The influence of

atmospheric conditions on the leakage current of Ceramic insulators on the Colombian Caribbean

coast," Environmental Science and pollution Research, Vol.22,No.4,PP.2526-2536,2015

[6]	Z . Zhang, X. Jiang, H. Huang, C. Sun, J. David, W. Gao, "Study  on  the  wetting  process  and

its influencing factor on Pollution deposited on different insulators based on leakage current,"

IEEE Trans. Power Del, Vol.28,No.6,PP678-684,2013.

[7] 	A . Arshad, A. Nekahi, S. Mc Meekin, M. Farzaneh,"Flashover characteristics of Silicon Rubber

sheets under various environmental conditions," Energies,Vol.9,No.9,PP.683-692,2016.

[8]	Z . Yang, X. Jiang, Z. Zhang, D.Zhang, Y.Liu,"Electrical property of different types of Insulator

string under typical Pollution constituents," IEEE Annual report Conference on Electrical insulation and Dielectric Phenomena, PP.170-175,2015.

[9]	D. Huang, W. LU, Y. Deng, J. Ruan, X. Ziteng, "Ca SO4 Content in contamination influence on

AC pollution Flashover characteristics of XWP2-160 Porcelain insulators string," IEEE

International Conference on high Voltage Engineering and application (ICHVE), PP.9807-

9816,2018.

[10]	Y. Wang, S. Song, Y. Luo, L. Xiao, D. Zhang, S. Wang, Q. Chen, HE.Zhenghao,"Experimental

research on AC flashover performance of Smearing insulator under Sea- Salt pollution," Insul. Surge Arresters, Vol.5,PP.11-15,2015.

[11]	S. Yang, W. Zhou, J. Yu, C. Zhou, H. Hu, B. Wang, C. Yang, "Influence of Glucose as a

Contaminant on discharge characteristics of HVAC insulators," IEEE Trans. Dielectr. Electr.

Insul.Vol.23, No.1, PP.394-402,2016.

[12]	S. Arumugam, PS. Neubaver, T.Schoenemann,"Dielectric and partial discharge investigation on

Ceramic insulator Contaminated With condensable Hydrocarbons," IEEE Trans. Dielectr. Electr. Insul, Vol.21, No.6, PP.2512-2524,2014.

[13]	J. Wang, K. Wang, L. Zhou, S. Yao, C. Fang, "Natural Contamination of XP-70 insulators in

Shenzhen, China," IEEE Trans. Dielectr. Electr. Insul, Vol.23, No.1, PP.349-358,2016 .

[14]	OE. Gouda, AZ. El Dien,"Experimental Techniques to Simulate naturally Polluted high Voltage

Transmission line insulators," IEEE Trans. Dielectr. Electr. Insul, Vol.23, No.5, PP.2199-

2205,2014.

[15]	M. Ali, R. Hackam,"Recovery of hydrophobicity of HTV Silicon Rubber after accelerated aging

in saline Solutions," IEEE Trans. Dielectr. Electr. Insul,Vol.16,No.1, PP.812-851,2009.

[16]	International Electrotechnical Commission (IEC Standard) 60060-1, 3rd ED," High voltage test

techniques- partI: general Definition and test requirements," IEC press Geneva, Switzerland, 2008.

[17]	International Electrotechnical Commission (IEC Standard) 60507,  "Artificial Pollution test on high

voltage insulators to be used on AC systems," IEC Press, Geneva , Switzerland; 1991.

[18]	International Electrotechnical commission (IEC Standard) 60815, "Selection and Dimensioning of

high voltage insulators intended for use in Polluted conditions," IEC Press, Geneva , Switzerland,  2008

[19]	LM. Wang, G. Wang, R. Hang, "Cleaning effect of rainfall on surface contamination of

Insulators," Power syst. Technol, Vol.39 PP.1703-1708.

[20]	Z. Zhang, D. Zhang, W. Zhang, C. Yang, X. Jiang, J. Hu, "Flashover performance of insulator

string with fan- shaped non uniform pollution," IEEE trans. Dielectr. Electr. Insul.Vol.22, No.1,

PP.177-184,2015.

[21]	A. Arshad, MA. Mugal, A. Nekahi, F. Umer, "Influence of single and multiple dry bands on

Critical Flashover voltage of Silicon Rubber outdoor insulators: Simulation and experimental

Study," Energies, Vol.11, No,13, PP.17-34,2018.

[22]	A. Arshad, A. Nekahi, SG. Mac Meekin, M. Farzaneh, "Effect of Pollution Severity on electric

field distribution along a polymeric insulators," IEEE 11th International conference on

properties and application of dielectric materials (ICADM),PP.613-615,2015.

[23]	Z. Jiang, X. Jiang, Z. Zhang, Y. Guo, "Investigating the effect of rainfall parameters on the self-

cleaning of polluted suspension insulators: Insight from China," Energies, Vol.10, No.5,

PP.607-612,2017.

[24]	HM. Bengesmia, N. Ziou, A.Boubakeur,"Experimental Study of Pollution effect on the behavior

of high Voltage insulators under AC Current," Frontiers in Energy, Vol.13, No.49. PP.1-9,2017.

[25]	R. Caslillo- Sierra, O. Oviedo- Trespalacios, JE. Candelo, JD. Soto, "Assessment of the risk of

failure of high  voltage  substations  due  to environmental  conditions  and  pollution  on

insulators," Environmental Science and Pollution Research. Vol.22, No.13, PP.9749-975,2015

[26]	Z. Zhang, X. Jiang, Y. Chao, C. Sun, "Influence of  low  atmospheric  pressure  on AC pollution

flashover performance of various Types of insulators," IEEE Trans. Dielectr. Insul. Vol.17, No.2, PP.425-432,2010.

[27]	MM. Hussian, SH. Farokh, SG. McMeekin, M Farzaneh,"Risk assessment of Failure of Outdoor

High Voltage polluted insulators under combined stresses near shoreline," Energies, Vol.10, No.10, PP.1661-1682,2017.

[28]	R. Castillo- Sierra, O. Oviedo- Trespalacios, JE.Candelo,JD. Soto,"Modelling leakage current of

Ceramic insulators subject to high pollution levels for improving maintenance activity," DYNA, Vol.85, No.204, PP.364-371,2018 .

[29]	MR. Salam, SP. Ang, F. Wen, M. Fdil, HA. Hadi, QM. Rahman, W. Voon, "Camparison  of

pollution level of Aged porcelain and Silicon Rubber insulators," Annual report Conference on

Electrical and Dielectric phenomena,PP.225-228,2015.

[30]	C. Wang, T. Li, Y.Tu, Z .Yuan, R. Li, F. Zhang, B. Gong,"Heating phenomenon in unclean

composite insulators," J. Eng. Fail. Anal, Vol.50, PP.48-56,2016.

[31]	SC. Oliveira, E. Fontan, FJ. Cavalcanti, "Real time Monitoring of the leakage current of 230 kv

glass insulators during washing," IEEE Transactions on power delivery. Vol.24, No.4,

PP.2257-2260, 2009.