International Journal of Electrical and Computer Engineering (IJECE)

Vol.x, No.x, September 201x, pp. xx~xx

ISSN: 2088-8708
(    
31
[image: image35.png]80 w029
70 5
5

£ 7o
g 50 s
s

< 40 S
2 30 ]
[} 389
20 b
b

10 i

o hi

5

0 20 40 60 80 100 120 s

Distance from Origin of Profile (m)






44
[image: image36.png]alTaln (g [ a nl

D0An0RNN000

0O 20 40 60 80 100 120
Distance from Origin of Profile (m)

1756
115
1055
%95
En
74
a3
753
892
832
574
514
450
390
30
%9
209
14z
88
27




     
( 

       ISSN: 2088-8708

43
IJECE 
ISSN: 2088-8708
(

Assessment of Step and Touch Voltages for Different Multilayer Soil Models of Complex Grounding Grid

Srete Nikolovski*, Goran Knežević *, Zoran Baus
* Department of Power Engineering, Faculty of Electrical Engineering, Osijek, Croatia
	Article Info
	
	ABSTRACT 

	Article history:

Received Jun 12th, 201x

Revised Aug 20th, 201x

Accepted Aug 26th, 201x


	
	In this paper the influence of different soil models on step and touch voltages are presented. Soil resistivity is the basic characteristic of soil which affects a number of parameters (temperature, humidity, salt content). Basic methods of measuring soil resistivity presented in this paper are: Wenner method, Schlumberger method, General method, Driven rod (3-probe) method and the Dipole-Dipole method. Soil resistivity measurements are used to obtain an equivalent soil model (uniform model, two-layer horizontal model, multi-layer horizontal model, vertical model and others). The CDEGS software package is used for computing GPR (Ground Potential Rise), touch and step voltage with several different soil models. The resulting effect of soil models on the grounding resistance, GPR at the surface, touch and step voltages are shown. The 3D spatial distribution and 2D presentation of all characteristic values for safety analysis are presented and plotted.

	Keyword:

Grounding grid

Soil resistivity models 

Ground potential rise
Step voltage

Touch voltage

Safety  limits
Computer simulation
	
	

	
	
	Copyright © 201x Institute of Advanced Engineering and Science. 
All rights reserved.

	Corresponding Author:

Srete Nikolovski 

Department of Power Engineering
Faculty of Electrical Engineering, Josip Juraj Strossmayer University of Osijek

K. Trpimira 2B, 31000 Osijek, Croatia
Email: srete.nikolovski@etfos.hr


1. INTRODUCTION 

The primary task of this paper is to show how different models of soil affect the calculation of the grounding. Grounding system is an important part of every power system, which is required to ensure proper operation of electrical equipment, ensure the users’ security of these devices, and to take away short circuit currents or lightning [1]. To create a better model of the soil, it is necessary to know the characteristics of the soil. The most important characteristic of the soil is a specific soil resistivity, whose amount can be obtained by one of the techniques of measuring specific resistance. [2],[3] The completed model of the soil affects further the type and dimensions of the grounding and the depth to which it will be buried. Use of computer software for modeling and calculation of grounding has greatly facilitated and ensured more accurate models of soil and ground calculation compared to previously used empirical and graphical methods of soil modeling. CDEGS (Current Distribution, Electromagnetic Fields, Grounding and Soil Structure Analysis) is software package composed of eight different modules that offer a complete grounding analysis. [4]

When grounding an object (power plants, substations, transmission lines, networks, etc.), the assumption is that the soil is a good conductor and that the current will freely flow through it. However, this may not be so, as the conductors of different materials are characterized by different specific resistances and the same happens with the ground. So, like any conductor, the soil in electrical terms is characterized by resistance which provides the passage of current. The resistance of the soil can be defined as the resistance between the opposite sides of the cube floor with a length of one meter site. The general soil resistivity is very high compared with the specific resistance of classic metal conductors. For different soil types, specific resistivity takes the value of several ohm-meters to several thousand ohm-meters
2.
MAIN CHARACTERISTICS OF SOIL


When grounding an object (power plants, substations, transmission lines, networks, etc.), the assumption is that the soil is a good conductor and that the current will freely flow through it. However, this may not be so, as the conductors of different materials are characterized by different specific resistances and the same happens with the ground. So, like any conductor, the soil in electrical terms is characterized by resistance which provides the passage of current. The resistance of the soil can be defined as the resistance between the opposite sides of the cube floor with a length of one meter site. The general soil resistivity is very high compared with the specific resistance of classic metal conductors. For different soil types, specific resistivity takes the value of several ohm-meters to several thousand ohm-meters. Fig. 1. shows how specific soil resistivity changes depending on the percentage change in the content of moisture, salt and different temperatures. [5]

[image: image1.emf]1 2 3 4

5 6 7 8 9 10

%

%

0 5 10 15

20

25 30

35

40

45

-25 -20

-15 -10

-5 0 +5

+10 +15 +20

°C

salt

humidity

temperature

50

100

500

1000

5000

 ρ [Ωm]

temperature

humidity

salt


Fig. 1. Dependence of soil resistivity ρ on the percentage of moisture, salt and temperature

Also the frequency can have the influence on soil properties and the grounding impedance which is presented in [7]

3. TECHNIQUES OF MEASURING SPECIFIC SOIL RESISTIVITY 

Measurement of specific soil resistivity is performed in such a way that the current is let go through two outer probes, current probes, while on the two probes which are in the same direction located between them, the voltage (potential) probes, the amount of voltage is measured. [8] Based on the released current and measured voltage, using Ohm's law, the resistance value is calculated, and, depending on the geometry of the method used to measure, the value of the apparent specific soil resistivity in Ohm – meters is calculated. In chapters A-E different methods of soil resistance measurement are shown. Wenner's method of measuring specific ground resistance is presented in Fig.2. Schlumberger's method of measuring specific ground resistance is presented in Fig. 3

[image: image2.emf]a

a a

b

V

I

P

1

P

2

S

1

S

2


[image: image3.emf]b

V

I

P

1

P

2

S

1

S

2

c

d

c


Fig. 2. Wenner’s method of measuring specific resistance   Fig. 3. Schlumberger’s method of measuring specific resistance 
General method of measuring specific ground resistance is presented in Fig. 4 and Dipol-Dipol method of measuring specific ground resistance is presented in Fig. 5 


[image: image4.emf]b

V

I

P

1

P

2

S

1

S

2

e f g

V

      
[image: image5.emf]b

V

I

P

1

P

2

S

1

S

2

a

na

a

V


Fig. 4. General method of measuring specific resistance    Fig. 5. Dipol-Dipol method of measuring specific resistance

3-Probe method of measuring specific ground resistance is presented in Fig. 6. The main difference from previously elaborated methods is that in this method instead of 4 probes only 3 probes are used for determining the ground resistance. 


[image: image6.emf]b

I

P

2

S

1-

P

1

S

2

V

b

2

0,62D

D

d


Fig. 6. 3 Probe method of measuring specific ground resistance 

4. SOIL MODELS
Interpretation and development of adequate model of the soil based on the measured values ​​of the apparent specific soil resistivity is one of the most challenging parts after performing measurements. In practice, the soil is usually modeled as a single layer (uniform), or as a two-layer and horizontal in relation to the surface of the soil. In more complex configurations, it is necessary to use horizontal multi-layer soil model [8], [9]. There may be special configurations of the soil, for example, when there is an exponential change in specific soil resistivity, vertical stratification, and regular or irregular volumes of soil with different specific resistance of the surrounding soil. However, such configurations are very rare in practice and usually installation of grounding in such soil tends to be avoided.

4.1.  Single layer-unuform soil modell
 Single-layer soil model (Fig. 7) approximates the ground as homogeneous, that is, of constant resistance.

[image: image7.png]



Fig. 7. Single-layer soil model 

Such model of soil is justified to be used when it is established by measurements that the apparent resistance of the soil does not vary significantly with increasing depth of measuring, or if it is not about a minor grounding system, so that certain omissions and approximations are allowed. An approximated single model of soil, or its resistance, can be obtained by taking the mean of all the measured apparent soil resistances, as shown in (1).




[image: image8.wmf]n

n

a

a

a

a

)

(

)

3

(

)

2

(

)

1

(

...

r

r

r

r

r

+

+

+

+

=




   
        (1)

where the numerator represents the sum of the apparent resistances on different distances and the denominator represents the total number of measurements. Another method for determining the resistance of a single-layer soil is according to (2).


[image: image9.wmf]2

min

max

r

r

r

+

=





               (2)
     where ρmax is the maximum apparent resistance measured (Ωm), and ρmin the minimum apparent resistance measured (Ωm).

4.2.  Two-layer model of horizontal soil 
Two-layer soil model consists of the upper layer of the final depth h and the specific ρ1 resistance and the lower layer of infinite depth and specific resistance ρ2, [10], [11]  Fig. 8.
[image: image10.png]



Fig. 8. Two-layer horizontal model
The difficulty in using this model is a mathematical determination of the depth of the first layer due to variations in the structure and properties of the soil. Methods used to determine the parameters of two-layer horizontal soil (ρ1, ρ2, h ) on the basis of measuring specific soil resistivity can be classified into two groups: empirical and analytical. Determination of the parameters of the horizontal two-layer soil is analytically made by applying mathematical formulas and functions (3), (4) and (5).



[image: image11.wmf]ï

ï

þ

ï

ï

ý

ü

ï

ï

î

ï

ï

í

ì

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

÷

ø

ö

ç

è

æ

×

×

+

-

÷

ø

ö

ç

è

æ

×

×

+

+

×

=

å

¥

=

1

2

2

1

2

4

1

2

1

1

4

1

n

n

a

a

h

n

a

h

n

K

r

r




          (3)





[image: image12.wmf]1

2

1

2

r

r

r

r

+

-

=

K





          (4)

[image: image13.wmf]å

=

ú

û

ù

ê

ë

é

-

=

N

i

mi

mi

i

h

f

1

2

2

2

1

))

(

(

)

,

,

(

r

r

r

r

r





          (5)
where K is the reflection coefficient, ρmi measured value of specific soil resistivity and ρ(i) an estimated value of specific resistance of the soil.

Another way of parameter determination is by using Sunde's graphical method (Fig. 9), which can roughly estimate the parameters of the two-layer horizontal soil without the use of computer or sophisticated equations.

.
[image: image14.png]1000 1000
500 r— 500
200 =200
—T |
100 / 100
=
50 - 50
20 20
10 10
: W am ;
g 2 2
~ i 1
SN
0.5 05 ..
i N
0.2 0.2 <
0.1 0.1
0.05 — 0.05
0.02 0.02
0.01 N 0.01
0.005 0.005
0.002 0.002
0.001 0.001

d 2 031 2 5 10 20 50 100 200 500 1000 2000 5000
a’h




Fig. 9. Sunde’s curves for determining parameters of two-layer horizontal soil 

4.3.  Three-layer model of horizontal soil 
Horizontal three-layer ground model is shown in Fig. 10. In this case, the soil consists of 3 layers, where each layer is characterized by the accompanying specific resistance and thickness of the layer until the last 3th, which is of an infinite thickness. [4], Determining parameters of multi-layer models requires the use of computer programs and advanced mathematical functions (complex Fig. methods, advanced integrated Taylor’s and Simpson’s formulas) because the calculation in relation to the single or two layer soil model becomes significantly complicated. The other two most common models of soil that occur in reality are vertical (Fig. 11) two-layer or multi-layer soil model and the soil model in which the specific soil resistivity changes exponentially with depth.

[image: image37.png][t w0

0O 20 40 60 80 100 120
Distance from Origin of Profile (m)

184
123
1063
1002
844
20
a9
758
697
87
576
515
454
93
B2
274
211
150
89
28




[image: image15.png]


  
Fig. 10. Three-layer soil model


Fig. 11. Two-layer vertical soil model

     After determining the apparent specific resistivity of each vertically oriented layer, ρ1, ρ2, the equivalent specific resistance, ρe, of the adjacent vertical tiers can be determined ( 6 ) [11] .

  
[image: image16.wmf]1

2

2

1

2

1

r

r

r

r

r

×

+

×

×

×

=

S

S

S

e

 



              (6)
Soil with an exponential change in specific soil resistivity with depth is determined by the specific resistance on the surface, ρ1, specific resistance of the deepest part, ρ2, and the coefficient λ. The apparent specific resistivity, ρa, for such soil and Wenner's way of measurement is calculated according to (7).

    
[image: image17.wmf])

2

(

)

(

1

2

2

a

a

a

e

e

l

l

r

r

r

r

-

-

-

×

×

-

-

=




              (7)
5. SIMULATION OF THE INFLUENCE OF DIFFERENT SOIL MODELS ON GROUNDING SYSTEM PERFORMANCE

Software package CDEGS is a collection of integrated engineering software tools for accurately analyzing problems involving grounding, electromagnetic fields, electromagnetic interferences, and various aspects of cathodic protection. CDEGS software package nowadays consists of eight engineering modules, and in this study the following two are used: RESAP and MALT. RESAP module is used to determine the equivalent model of the soil based on the selection of the measuring method and the measuring values ​​of the apparent resistivity (or resistance) of the soil. MALT module is used for the analysis of low frequency grounding. [4] Modeling of the soil was performed in RESAP module. Measurements done by Wenner’s four probe method are entered in RESAP module. In the selection of soil types that is to be modeled on the basis of the measurements is selected. In the first case, the soil is modeled as a single-layer (Fig. 12), in the second case, the soil is modeled as horizontal two-layer (Fig. 13) and in third case as  horizontal three-.layer (Fig. 14)
For measurement were used data from [13] 

Table 1. Measurements of soil resistivity using Wenner’s method
	Time
	Spacing (a) [m]

	Measured resistivity

 ρ [Ωm)

	1
	1
	125.0354

	2
	1.5
	108.6677

	3
	2
	85.3257

	4
	2.5
	69.4292

	5
	3
	55.4177

	6
	4
	37.4478

	7
	5
	30.7876

	8
	6
	26.0124

	9
	7
	22.8708

	10
	8
	16.0850

	11
	9
	17.5301

	12
	10
	16.3364


[image: image18.emf]0

20

40

60

80

100

120

140

0 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18

Apparent Resistivity (Ohm-meters)

Inter-Electrode Spacing (meters)


Fig. 12. Simulation results of single-layer soil model
If the soil is modeled as single layered, the uniform soil resistivity ρ = 39.42503 Ωm is obtained. Deviation of theoretical apparent resistance from the measured apparent resistances is expressed by RMS-error (root-mean-squared error), RMS error between measured and calculated resistance in this case is 36.48 %, which is a significant error.

[image: image19.emf]10

30

50

70

90

110

130

0 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18

Apparent Resistivity (Ohm-meters)

Inter-Electrode Spacing (meters)


Fig. 13. Simulation results of two-layered horizontal soil model from measured results
Table 3. Specific resistance and thickness in two-layer soil model
	Number of the layers
	Specific soil resistance            ρ [Ωm]
	Thickness of the layer [m])

	1
	126.0062
	1.816445

	2
	15.48484
	∞


RMS-error when the soil is modeled as a two-layer is 7.44%. By the amount of RMS-error, it is obvious that two-layered model corresponds more to the model of the real soil on which measurements are performed than to the previous case of a single-layer soil model. When the three-layer model is used, RMS-error is 6.09%. Three-layered model corresponds best to the model of the real soil on which measurements are performed in respect to the single and two-layered soil models.

[image: image20.emf]0

20

40

60

80

100

120

140

160

0 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18

Apparent Resistivity (Ohm-meters)

Inter-Electrode Spacing (meters)


Fig. 14. Simulation results of three-layered horizontal soil model from measured results

Table 43. Specific resistance and thickness in three-layer soil model

	Number of the layers
	Specific soil resistance ρ [Ωm]
	Thickness of the layer [m])

	1
	150.8457
	0.990462

	2
	64.09731
	1.694774

	3
	14.05551
	∞


6. SIMULATION RESULTS  FOR SAMPLE CASE

Grounding grid is placed at a depth of 0.8 m. It is meshed grid made up of 12 transverse and 9 longitudinal grounding strips, which are connected to each other and form a network of overall 110 × 80 m. [6] The length of the Fe/Zn conductors 30×5 mm are 1950 m. Additionally, on the connecting grounding grid 25 properly distributed grounding rods are placed in length of 3 m. The diameter of rods is 50.8 mm. The current that is injected into the grounding system is Ik = 7480 A.

[image: image21.png]



Fig. 15. Model of the ground system used in simulation 


The grounding grid from Fig. 15 is buried in the depth of 0.8 m in a single-layer soil model obtained by simulating in Fig. 12. Running the simulation provides the following report. Resistance of single-layered soil is 39.425 Ωm. Resistance of the grounding grid is Ri= 0.1867 Ω.  The potential of the grounding grid is GPR= 1396.8 V.  

[image: image22.png]



Fig. 16. 3-D profile of GPR for a grid in a single-layer soil model 

[image: image38.png]0 20 40 60 80 100 120
Distance from Origin of Profile (m

)

1207
1229
1162
1005
1027
96.0
893
825
758
691
623
556
488
4241
354
286
219
152
84
17




According to the selected standards 70KG-IEEE, the body weight of 70 kg an fibrillation current according C3-IEC and body resistance according IEC that is located on the surface can be exposed to the maximum touch voltage of 292.2 V and steps voltage of 358.2 V for the fault clearing time of 0.5 s. In this case there is no additional surface layer on the soil.

[image: image23.png]@
3

520
493
465
439
412
385
357
330
303
5
249
2
195
167
140
13

£

5
0 2
0 20 40 60 80 100 120 s

a o N
3 3 o

©
S

Distance (m)
8

)
o o

Distance from Origin of Profile (m)




Fig. 17. Touch voltage for single-layer model     
Fig. 18. Step voltage for single-layer model 

From Fig. 17. and Fig. 18. in spite of relatively high GPR, touch and step voltages are in the permissible security limits. By placing the grounding grid to a depth of 0.8 m in the two-layer model of soil, obtained by simulation in Fig. 13, the result will be a network composed of connecting ground strips in the first layer of greater resistance, while rods reach the second layer of lower resistance. Running the simulation provides the following report. 

[image: image24.png]



Fig. 19. 3-D profile of GPR for a grid in two-layer soil model 

The resistance of the first layer is 150.8457 Ωm. Resistance of the second layer is 64.0973 Ωm. Resistance of the third layer is 14.055 Ωm  Thickness of the first layer is 0.99046 m, thickness of the second layer is 1.694774 m. Resistance the grounding grid is Ri= 0.11294 Ω. The potential of the grounding grid GPR= 844.76 V. In the two-layer model of the soil, touch voltage and step voltage are slightly higher, but still in permissible limits since the amount of the maximum touch voltage is 340.5 V and step voltage is 551.5 V and are obtained from security threshold computation for fault clearing time of 0.5 s.
[image: image39.png]80
70

60

E

- 50

< 40

2 30
20
10

0 20 40 60 80 100 120
Distance from Origin of Profile (m)

2218
2159
2040
1921
1803
1684
1565
1446
1327
1208
1089
970
851
732
613
494
375
256
138
19




[image: image25.png]80

70 PO ey e et
ESD*""”"""
=507 P ona'saea
EAD*”"”"""
gsoi O St S S S e S
20 PRt et e
10 | PRI e e
0l

0O 20 40 60 80 100 120
Distance from Origin of Profile (m)

494
an
449
426
403
381
358
33
313
290
267
245
222
199
77
154
131
109

86

63





           Fig. 20. Touch voltage for two-layer model                  Fig. 21. Step voltage for two-layer model
At the end, the grounding grid from Fig. 15 is buried in the depth of 0.8 m in a three-layer soil model obtained by simulating in RESAP module. The resistance of the first layer is 126.0062 Ωm. Resistance of the second layer is 64.0973 Ωm. Resistance of the third layer is 15.4848 Ωm. Thickness of the first layer is 0.99046m. Thickness of the second layer is 1.69477 m. Resistance of the grounding grid is Ri= 0.11184 Ω. The potential of the grounding grid is GPR= 836.55 V

[image: image26.png]



Fig. 22. 3-D profile of  GPR for a grid in three-layer soil model 

In the three-layer model of the soil, touch voltage and step voltage are smaller, and are in permissible limits since the amount of the maximum touch voltage is 354.4 V and step voltage is 607.0 V and are obtained from security threshold computation for fault clearing time of 0.5 s.
[image: image40.png]


[image: image27.png]80

701 e
PRI o = e
£ omt
5 50

8 S - 5
€40 O Dt S S0
Z O o )
6307 E S e S
20+

10 PRy
04

0O 20 40 60 80 100 120
Distance from Origin of Profile (m)

519
495
a4
451
a2

361
33
316

mn
249

181
159
136
14

£l





    Fig. 23. Touch voltage for three-layer model     

Fig. 24. Step voltage for three-layer model 

If the dangerous situation for personnel during the fault conditions over the grounding grid want to be avoided, usually isolation surface layer of crushed stone can be used [10] [11] . For that situation safety values for touch and step voltages are much higher. Touch permissible voltage is 673.9 V and step permissible voltage 1884.8 V.

[image: image28.png]Fault Clearing Time (sec) Body Resistance IEC Percentage:

Define Safety Scenario.. | |  IEEE Percentage:

@ EC € 100% (hand-to-hand)
Fibrillation Current Calculation Method " UserDefined @ 75% (hand-to-2 feet)

C34EC < € 50% (2 hands-to-2 feet)

e e
S Saface Unfom Sl Loyr Rty Ohm
Foot Resistance Calculation Method Decrement Factor

IEEE 51d.80-2000 <] Extra Resistance (shoe. glove. etc) |:| ® B

e e e € Computed

IEC Options.

EC Stondard Revison 2005 <] || e ot
Body Resistance Curve 95% of Population Exceeds Curve v e

Contact Moisture Dy B

1

[

Reforence Insulaing Surfoce Loyer etz [ ]
Suface Layer Thickness: |8 [Contmetors =] [
n Softwore.

b o)

Surface Resis

Safety Limits (Volts) Save Settings r—
Safe Touch Voltage: 606.3 | Generate Safety | & for MALT Only
Safe Step Voltage: 1817.2 | Thieshold Linits oK
and Report | for MALT, MALZ and HIFREQ
Cancel





Fig. 25.  Safety Calculations Table

If the influence of vertical soil model and soil resistivity wants to be investigated on step and touch voltages next data are used according to the Fig. 11
Table 4. Specific resistance and thickness in vertical two-layer soil model
	Number of the layers
	Specific soil resistance ρ [Ωm]
	Thickness of the layer [m]
	Coordinates



	1
	126.0062
	∞
	Angle θ
	Xp
	Yp

	2
	15.48484
	∞
	90o
	95
	85


The main grid potential rise (GPR) is 1498.2 V, because the most of grounding grid is in left higher resistivity soil. The asymmetry and the influence of vertical soil model on touch and step voltages cannot be clearly visiable since grounding grid is on the same GPR.

[image: image29.png]



Fig. 26. 3-D profile of  GPR for a grid in vertical soil model 

[image: image30.png]0 20 40 60 80 100 120
Distance from Origin of Profile (m)

646
612
579
545
511
a78
444
410
376
343
300
215
281
208
174
140
107

73

39





Fig. 27. Touch voltage for two–layer vertical soil model     Fig. 28. Step voltage for two–layer vertical soil model 

Touch and step voltages in two–layer vertical soil model are higher since the most of grounding grid is buried in higher soil resistivity part ρ1 and small asymmetry can be seen on 2D plots. The potentials along the vertical layer boundary must be continuous. Knowing that the soil potential is proportional to the product of its resistivity (ρ) and the leakage current (I), the condition ρ1 * I1 = ρ2 * I2  must be valid at the interface between both vertical layers, where the subscripts 1 and 2 stand for each vertical soil layer. For the aim to examine the influence of the two layer vertical soil model with high difference in soil resistivity on touch and step voltage model next data are used.

[image: image31.png]0 20 40 60 80 100 120
Distance from Origin of Profile (m)

045
4826
a107
as88
4469
4350
4231
a2
3993
3874
3755
3637
3518
3399
3280
3161
3042
2023
2804





Fig. 29.  GPR for two-layer vertical model                   Fig. 30.  Touch voltage for  two-layer vertical model 

Since the potentials along the vertical layer boundary must be continuous, this explains why there are no sharp variations in the surface potentials from one vertical layer to the other, even in the case of a high resistivity contrast. However, if the spots on the above 2D plot are carefully looked at, it can be noticed that the potentials are not exactly symmetrical, which is actually a consequence of the used vertical soil structure.
If we compare 3-D profiles of potential grounding for the grounding grid in uniform soil model (Fig. 16) and ground device in a two-layer soil model (Fig. 19), and three-layer soil model (Fig. 23), the first difference is evident in the amount of earth potential. When the soil is modeled as a single-layer, the grounding potential of the system (GPR) is 1396.8 V, while in the case of the same grounding system placed in a two-layer soil model, the grounding  potential is 844.76 V and in a three-layer soil model is 836.55 V. The potential of the grounding device is equal for the entire grounding and all metal parts attached to it. As the GPR directly depends on the potential of the grounding grid and soil models in the case of a single-layer model of the soil, the maximum grounding potential is ≈1396 V, and in the case of two-layer soil model, ≈844.7 V. Therefore, in the two-layer soil model 60.5 % less grounding potential is achieved in relation to the single layer model of soil. Difference between two-layer and three-layer model in GPR is minimal GPRtwo-layer=1.009GPRthree-layer. Such a difference between single-layer and two-layer results could have been expected because the model in a single-layer soil has a large RMS-error and the values of the potential of the grounding grid can be considered more accurate and closer to those expected in reality if two-layer or three-layer model is used. 
Another difference is evident in the appearance of the 3-D profile of GPR. For a single-layer soil model 3-D profile of the grounding potential at the ground is more balanced and has less so called "spikes" (the place where the vertical Fe / Zn strips merge with each other to form a network). In the two-layer soil, 3-D profile is not as uniform and "spikes" are much larger. This is because the rods that are connected to the network of the grounding grid reach a better conductive lower layer. In both cases, the maximum potential values of the land are in the area of ​​the central part of the grounding device and they gradually decrease toward the ends. The same situation is with a three-layer soil model.

If we compare the prospects of 2-D profile of a touch voltage (the difference between the potential of the grounding grid and potential of the earth) for the grounding grid in one single-layer model of the soil (Fig.17.), and the grounding device in a two-layer model of the soil (Fig.18.) and three-layer soil model (Fig.23.), the "bellies" in the case of two-layer soil model are more visible. This is because of the aforementioned large "spikes" and irregularly shaped potential of grounding that causes somewhat greater potential difference, or touch voltages. The reason that the amount of touch voltages in both cases on the area of ​​the grounding device will not exceed the safety limit is because the grounding device is oversized, a safety factor is further increased by filling the surface 5 cm by soil resistivity material resistance of 1000 Ωm (gravel). Problematic values ​​appear just outside the grounding device but this is resolved in such a way that around the area where the device is buried, a fence is put in order to prevent access and possibly exposure to hazardous touch voltage. The fence must have its own grounding and should not be connected to the existing device because in this way the potential would be displayed on the area where the potential of the earth is low which would cause dangerous touch and step voltages.

Step voltages in the case of all three models (Fig. 18, Fig. 21 and Fig.24), are far below the value that would be considered dangerous, obtained according to the security settings, even outside the areas where grounding system is buried.

7. CONCLUSION
Modeling of soil based on the measurements of specific soil resistivity is left to the decision of that person who is in charge of it and on the basis of his assessment and experience, because there are no clearly defined rules for this area in Croatia. In practice, when modeling soil for grounding of electric power plants (substations), two-layer soil model proved to be good enough. With a single-layer model of the soil, the soil will be modeled well very rarely, as evidenced by simulations in this paper. Two-layer model may not be the rule by which to model the soil when grounding substation, and we must consider the possibility of modeling the soil as multi-layered depending on the estimation. Three-layer soul model do not effect so much in accuracy and safety so if it is not needed it could be avoided. 

For the vertical soil model can be concluded that the last results show small asymmetrical potentials, even with a very high resistivity contrast. In light of the above results, it seems that the asymmetry of the system has a greater impact on the asymmetry of the potentials than the resistivity difference between the vertical layers. Incorrect soil modeling leads to a relatively large difference in all important parameters in the grounding systems, as it is shown in this paper. As the modeling of soil is considered a complex task, it is recommended to use computers and computer software made for this purpose, as this will avoid additional errors resulting from the use of approximate graphical and analytical methods. 
ACKNOWLEDGEMENTS 
We would like to thank Marc-Andre Joyal, PhD from SES Technologies Ltd. Canada, for his help and valuable comment during the computations and simulations.
REFERENCES 
[1] IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System, The Institute of Electrical and Electronics Engineers, Inc., New York, 1983.

[2] IEEE Guide for Safety in AC Substation Grounding, The Institute of Electrical and Electronic Engineers, Inc., New York, 2000.

[3] IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System, The Institute of Electrical and Electronics Engineers, Inc., New York, 1983.

[4] CDEGS software, User Manual 2016 

[5] M.J. Wilt, N.E. Goldestein, “Dipole-dipole resistivity
 monitoring at the Cerro Prieto geothermal field,” Geothermal Resources Council, California, 1983.

[6] D, Dostal “Different sol models on transformer station 110710 Kv atation grounding system” graduate work , Faculty of electricak engineering Osijek 2018

[7] M. Mokhtari, Z. A. Malek, C. L. Wooi, „Integration of Frequency Dependent Soil Electrical Properties in Grounding Electrode Circuit Mode“  International Journal of Electrical and Computer Engineering (IJECE) Vol 6, No 2 April 2016
[8] E. Mombello, O. Trad, J. Rivera, A. Andreoni, “ Two-layer soil model for power station grounding system calculation considering multylayer soil stratification“,Electric Power Systems Research 37 (1996) 67-78
[9] J. Liu and F. P. Dawalibi "Detailed Parametric Analysis of Grounding System Performance in Two-Layer Soil Structures "Proceedings of the Seventh IASTED International Conference on Power and Energy Systems, Clearwater Beach, USA, Nov.r 28 – Dec. 1, 2004, pp. 370-375.
[10] J. Ma, F.P. Dawalibi, R.D. Southey, “On the equivalence of uniform and two-layer soils to multilayer soils in the analysis of grounding systems”, IEE Proceedings– Generation, Transmission and Distribution 143 (1996) 49–55.

[11] H. S. Lee, J. H. Kim, F. P. Dawalibi, and J. Ma,"Efficient Ground Grid Designs in Uniform and Two-Layer Soils," Korean IEE Transactions, 1997

[12] S. Vujevič, M. Kurtović, “Numerical analysis of earthing grids buried in horizontally stratified multilayer earth”, International Journal for Numerical Methods in Engineering 41 (1998) 1297–1319.
[13] R, Ibsaim, A, Ammar, ”Performance assessment and modeling of grounding grid”, Case study of Alkhom 400 kV substation, University Bulletin–Issue No.16- Vol. (1) February - 2014.
BIOGRAPHY OF THE AUTHORS
	
	

	[image: image32.jpg]



	Srete Nikolovski, PhD (IEEE M’1995, SM’2005) was born in Belgrade on October 1, 1954. He obtained his BSc degree (1978) and MSc degree (1989) in Electrical Engineering at the Faculty of Electrical Engineering, University of Belgrade and his PhD degree (1993) at the Faculty of Electrical and Computing Engineering, University of Zagreb, Croatia. He is a Full Professor at the Department of Power Engineering at the Faculty of Electrical Engineering, University of Osijek, Croatia. His main interests are power system protection, power system modeling, simulation and reliability. He has published 180 academic papers in journals and international conferences proceedings. He is IEEE Senior member of Reliability Society and PES Society.

	
	

	[image: image33.jpg]



	Goran Knežević, PhD, was born on September 1, 1984. He obtained his diploma degree in 2007 and PhD degree in 2013 from the Faculty of Electrical Engineering, J.J. Strossmayer University of Osijek, Croatia. He currently works as an Assistant Professor at the Department of Power Engineering at the Faculty of Electrical Engineering Osijek. His topics of research include electricity markets simulation, energy markets integration, power system economics and cost/benefit assessment, optimization of power system operation and power system analysis.

	
	

	[image: image34.jpg]



	Baus Zoran, (PhD), was born in Pozarevac on June 15, 1951. He obtained his BSc degree (1975), MSc degree (1987), in Electrical engineering and his PhD degree from the Faculty of Electrical and Computing Engineering, Zagreb, Croatia in 2004. His major fields of interest include intelligent control, fuzzy control and optimization and power system analyses. Currently he is a Full professsor at Power Engineering Department at Faculty of Electrical Engineering, J.J. Strossmayer University in Osijek, Croatia.


Journal homepage: http://iaesjournal.com/online/index.php/IJECE
IJECE  Vol. x, No. x,  September 201x :  xx – xx

Title of manuscript is short and clear, implies research results (First Author)















b
V
I
P1
P2
S1
S2
e
f
g
V



_1520517555.unknown

_1520517557.unknown

_1520517560.unknown

_1520517561.unknown

_1520517558.unknown

_1520517556.unknown











b
I
P2
S1-P1
S2
V
b2


0,62D
D


d



_1520517553.unknown











b
V
I
P1
P2
S1
S2
a
na
a


V
















a
a
a
b
V
I
P1
P2
S1
S2
















b
V
I
P1
P2
S1
S2
c
d
c



1
2
3
4
5
6
7
8
9
10
%
%
0
5
10
15
20
25
30
35
40
45
-25
-20
-15
-10
-5
0
+5
+10
+15
+20
°C
salt
humidity
temperature
50
100
500
1000
5000
ρ [Ωm]



temperature
humidity
salt



